| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |  |  |
|  | Documents Priority | Vendor to confirm that in case of contradiction between this TCL and offer; vendor confirmation of compliance through this technical clarification is governed and shall be followed by vendor after order. In such case offer won’t be considered as basis of any claim after order. |  |  |  |  |  |
|  | Deviation List | Bidder shall confirm his full compliance to meet all purchaser documents listed and attached to MR, code / standards listed in "BK-BK05-PEDCO-110-EL-MR-0003"as well as MR requirements. All deviations shall be listed in project deviation form, attach to MR, signed and stamped. Notes: 1-Any exception and deviation from the requirements of MR and the related specifications including referenced codes & standards shall be clearly declared by vendor in writing for purchaser’s approval at bid stage by using of the format included in “Letter Of Conformity”. Raising no deviation to any single requirement means full compliance of vendor quotation to that requirement. Purchaser has no responsibility to discover deviations or alternatives scattered over the proposal in addition to what proclaimed explicitly in deviation list; hence such deviation (if any) is disregarded and shall not be considered for vendor claim in future. (Vendor to confirm) 2- Bidder shall confirm that all MR attachments listed in MR are available for her for review at bid stage. 3-Considering items 1 & 2, please note that any deviation at detail stage will not be accepted by purchaser. |  |  |  |  |  |
|  | Documents Priority | Bidder to confirm his compliance with documents priority stated in MR. Any conflict between the documents shall be notified by bidder to purchaser and resolved by his agreement |  |  |  |  |  |
|  | Requirement For Documents | Bidder to confirm that documents required after purchase order shall be submitted in accordance with “RFD Form” attached to the MR. |  |  |  |  |  |
|  | Sub-Vendors | Bidder to confirm that Sub-Vendors shall be selected from Project’s approved AVL (MOP) |  |  |  |  |  |
|  | Specification | Bidder to confirm that surface preparation and painting of all equipment material including valves, pipes, fittings and everything within the package are in accordance with the project painting specification attached to MR. |  |  |  |  |  |
|  | Specification | Bidder to confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to the project specification attached to the MR. |  |  |  |  |  |
|  | Inspection and Test Plan | Inspection and Test Plan / Quality Control Plan and their related inspection level (Witness, Hold, Review and Approval) shall be at least in accordance with MR and all project requirement such as project ITP and “QA inspection and test” section of datasheets if any. Any deviation is not accepted unless otherwise specified in deviation list and approved by Purchaser. |  |  |  |  |  |
|  | Material Certificate | Bidder to confirm that for all pressure parts and those required special consideration or stainless steel as well as for supports the material certificate should be in accordance with EN 10204, 3.1 Material certificate for non-pressure parts shall be in accordance with EN 10204, 2.2. |  |  |  |  |  |
|  | Scope | Bidder shall confirm the scope of work and supply are fully in accordance with MR and its attachment with following items: 1- The consequences of HAZOP and SIL study shall be in vendor scope of supply and work. 2- Participation in technical meeting whenever it is necessary by Purchaser/Client to close engineering document after order is in vendor scope 3- Lifting beams (Spreader beams) for erection with sling shackle and etc. shall be designed and supplied by vendor 4- N2 preservation with pressure regulator, valve & flexible hoses during transportation & 18 months of site storage based on requirements in MR shall be in vendor scope of supply / work. 5- All utility conditions shall be as per document "Process basis of Design Document; Doc. No: BK-GNRAL-PEDCO-000-PR-DB-0001". Moreover, bidder shall consider utility noted condition as per project design data. If other utility condition is needed, whole required facilities is in vendor scope of work/supply. 6- Anchor bolts |  |  |  |  |  |
|  | Spare Parts | Vendor shall supply his spare parts as per the attached spare part list (as min): |  |  |  |  |  |
| MECHANIC |  |  |  |  |  |  |  |
|  | Document Requirement | Bidder to submit all required documents with tender as per “RFD Form” in the MR. For example below documents: 1-Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) 2-P&ID 3-GA DWG with outline dimensions and weights related to this project 4-Utility Consumption List 5- Diesel Engine datasheet and specification 6- Correction Curve for Diesel Engine 7- Reference and Experience List 8- Sub-Vendor List |  |  |  |  |  |
|  | Applied Standards | Applied Standards for equipment design, fabrication and test shall be listed. |  |  |  |  |  |
|  | Vendor’s Scope | Design and supplying of Heat Tracing and insulation if required to be in the vendor’s scope. |  |  |  |  |  |
|  | Inspection and Test | Test procedures and acceptance criteria will be checked after order with project specifications and related standards. Vendor to confirm to follow project standard and spec. |  |  |  |  |  |
|  | Applied Standards | IPS-M-PM-290 and ISO 3046 for diesel engine to be completely followed by vendor |  |  |  |  |  |
|  | Performance Requirement | The diesel engine continuous rating power available at the coupling, after de-rating required for the type of service, ambient temperature, fuel quality, altitude and etc. shall exceed the maximum power demand at 100% speed by not less than 10%. Maximum power demand is the sum of: • Maximum driven equipment absorbed power including test tolerance. • Transmission losses (e.g. shaft, bearing,, etc.). • Auxiliary power take-offs (e.g. oil pumps, etc.). Vendor to Confirm. |  |  |  |  |  |
|  | Mechanical Comments on Proposal | For comments on proposal please refer to “Mechanical Comments” attachment of this TCL. |  |  |  |  |  |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Specification & Standard | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. |  |  |  |  |  |
|  | DSH | Fulfilled & signed submitted data sheet should be prepared & sent. |  |  |  |  |  |
|  | Alternator | The origin of manufacture for alternator should be specified. |  |  |  |  |  |
|  | Ni-cd battery | The delivery time shall be specified. |  |  |  |  |  |
|  | Site condition | Vendor To confirm That All supplied material all in full compliance with Project site condition : BK-GNRAL-PEDCO-000-PR-DB-0001_D08– process design basis -Min/Max air temperature = - 5°C / + 52°C - Relative humidity = 100% - Altitude = 12.5 m a.s.l. - Climate = Dusty Please confirm. |  |  |  |  |  |
|  | priority | All The equipment’s shall be engineered, designed, manufactured, tested & installed in accordance with one of the following standards: LOCAL CODES & STANDARDS Iranian Petroleum Standard (IPS) INTERNATIONAL CODES & STANDARDS IEC (International Electrotechnical Commission) BS (British Standard) IEEE (Institute of Electrical & Electronics Engineers) API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards & codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes & Standards. Please confirm. |  |  |  |  |  |
|  | Scope of work | Minimum Scope of work & supply are in full compliance with Project Requirements. for Electrical has been Listed but not Limited to the following Items : - Full Engineering Services. - One Set Diesel Engine Generator Pkg. . - Power Panel According data sheet. - Control Panel . - Other items ACC to Spec for DEG Please confirm & Complete the List. |  |  |  |  |  |
|  | Stamped | Please stamp & return all attached documents & PMR. |  |  |  |  |  |
|  | Deviation | The deviation should be filled in project format. Please refer to page 14 of PMR. |  |  |  |  |  |
|  | Operating duty | Diesel Engine Generator Package shall be Design for continuous Operating Duty. Please confirm. |  |  |  |  |  |
|  | GAD | General Arrangement Layout shall be submitted with minimum dimensional drawings for below items : 1- Diesel Engine + Generator. 2- Power & Control Panels & Access Doors. 3- Battery Stand. 4-Other Main Equipment. Please confirm & submit in next proposal. |  |  |  |  |  |
|  | TBA | Attached TBA Table should be fill full & reply by vendor in native Excel sheet in next proposal. All required data & reference Documents shall be submitted in next proposal. Please confirm. |  |  |  |  |  |
|  | Accessories | All Required Cable Gland & Plugs are in Vendor Scope of work & shall be ISO metric threaded in accordance with IEC60423. Please confirm. |  |  |  |  |  |
|  | Cable type | Electrical Cable Type are as follow : Power : Cu/XLPE/SWA/PVC OR : Cu/XLPE/AWA/PVC Control : Cu/PVC/SWA/PVC RTD or PTC : Cu/PVC/ISCR/OSCR/SWA/PVC All Cable & Cabling inside the package Battery Limit are in Vendor SOW. Please confirm. |  |  |  |  |  |
|  | Scope of work | The proposal shall be completed. Documents such as “Deviation”, “ITP”, “Resume of projects”, “Sub-vendor list”, Data sheets”, “catalogue of Generator Control Panel” & other required shall be issued. |  |  |  |  |  |