## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-HV-PY-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1361 |  |  | Transmital Date: 9/5/2022
Document Title: Plumbing & Sewage Piping Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-1361 |  |  | Transmital Date: 9/5/2022
[5 empty] | CRS No: NISOC-CRS-BK-GNRAL-PEDCO-220-HV-PY-0001-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | عنوان نقشه مطابق نقشه طراحی شده اصلاح گردد (GRAND FLOOR FURNITURE PLAN - زیر PLAN به اشتباه درج گردیده.) |  | 1401/2294/304906 | 1401/08/19 | اعمال گردید.
2 | تراز اجرایی لوله کشی آب سرد و گرم مصرفی مشخص گردد. |  | 1401/2294/304906 | 1401/08/19 | اعمال گردید.
3 | محل قرار گرفتن شیرهای قطع و وصل نا مناسب می باشد. (بهتر است در کنار دیوار تعبیه گردد.) |  | 1401/2294/304906 | 1401/08/19 | اعمال گردید.
4 | لوله کشی ونت فاضلاب با در نظر گرفتن تعداد رایزر بیشتر اصلاح گردد ( جهت کاهش طول لوه کشی و عملکرد مناسب ونت) |  | 1401/2294/304906 | 1401/08/19 | اعمال گردید.
5 | لوله کشی فاضلاب به صورتی که فاضلاب از نزدیک ترین مسیر از ساختمان خارج گردد بازنگری شود. |  | 1401/2294/304906 | 1401/08/19 | با توجه به محل مشخص شده جهت اتصال سیستم دفع فاضلاب ساختمان به شبکه جمع آوری فاضلاب محوطه، ارتفاع بلوکاژ و طول بیشینه خط لوله سیستم فاضلاب با در نظر گرفتن شیب لازم، تغییر مسیر سیستم دفع فاضلاب که موجب تطویل مسیر خواهد شد، نیاز نمی باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: K.Ahmadi | Signature | M.Fakharian
| Date: 06/29/2022 |  |  |  |  | Date: 07/26/2023