## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-HV-PY-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1361 |  |  | Transmital Date: 9/5/2022
Document Title: Plumbing & Sewage Piping Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-1361 |  |  | Transmital Date: 9/5/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-220-HV-PY-0001_D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion | Clarification (By EPC Contractor) | Client Conclusion
1 | to add regulation valve after first pressure gauge and before inlet of water to building for valve box (this is for protection of exceed pressure above 4 bar) |  | BK-SUR-ENG-HVC-01-05842 | 2022-10-08 | Its not applicable. Because network pressure is under 4bar. |  |  | ok and closed | -
2 | to add condensate drain piping on this drawing-it is preffered to drain water discharged to green spaces (condensate pit inside of green space) |  | BK-SUR-ENG-HVC-01-05842 | 2022-10-08 | due to high numbers of split units and their distances, this is impossible to drain water discharged to green spaces. spilt drainage discharge to areas around building. |  |  | ok ,only add drain pipings on this draing | noted and done.
3 | since size of PEX-AL-PEX pipes (ISIRI 12753) in IMPERIAL and METRIC (regarding to inside diameter in camparison with steel pipe ASTM A53 ) are as follow 3/8" 17.1mm 16mm 1/2" 21.3mm 20mm 3/4" 26.7mm 25mm 1" 33.4mm 32mm ............... all sizes shall modify accordingly -for review and check |  | BK-SUR-ENG-HVC-01-05842 | 2022-10-08 | it has done according to vendors technical document and their tables for sizing of 5 layers piping. |  |  | Open for action :since piping design is based on inside diameter, and due to that the inside diameter of steel pipes are one size bigger than PEX-AL-PEX pipes, to prevent of any misunderstanding , piping size shall show in imperial system on the piping plan and table size, for example size 1/2" is 20mm fot pex-al-pex. therfore if piping size is 16 according to pex-al-pex this is equal to 3/8" and vice versa. | DW system pipe, sized based on outside diameter "PEX-AL-PEX" according vendor technical document that attached.
4 | same as item 3, PP pipe size (based on EN 1451) shall modify based on actual inside diameter (in camparison with steel pipe ASTM A53 )-for review and check |  | BK-SUR-ENG-HVC-01-05842 | 2022-10-08 | it has done according to vendors available sizes. |  |  | Open for action : same as reply for item 3 | According Basic document "sewage & vent system pipes should be PVC-U pipe". Sewage system sizing based on nominal pipe size that vendor technical documents released.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: K.Ahmadi | Signature | M.Fakharian
| Date: 06/29/2022 |  |  |  |  | Date: 07/26/2023