## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-HV-PY-0002-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0938 |  |  | Transmital Date: 14/MAY/2022
Document Title: HVAC System Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-0938 |  |  | Transmital Date: 14/MAY/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-220-HV-PY-0002-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | refer to owner letter number 01/2294/27253 dated 1401/01/28 ,for select of design wet bulb temperature based on MPO (Management and Planning Organization of Iran) published no.271 , if wet bulb shall change then calculation loads and equipment scheduel table for split unit must change consequently. this is for your reply and action (if it is required) |  | BK-SUR-ENG-HVC-01-04925 | 2022-06-29 | noted & done.
2 | to add one column for actual cooling load , and in table remark that the split units shall work for T3 categoury and cooling load shall de-rate 30% in compare with T1 rating. |  | BK-SUR-ENG-HVC-01-04925 | 2022-06-29 | noted & done.
3 | ducting elevation shall mention |  | BK-SUR-ENG-HVC-01-04925 | 2022-06-29 | noted & done.
4 | split unit installtion level shall mention |  | BK-SUR-ENG-HVC-01-04925 | 2022-06-29 | noted & done.
5 | in EWH table ,stand change to floor stand |  | BK-SUR-ENG-HVC-01-04925 | 2022-06-29 | noted & done.
6 | to add table schedule for air distribution device (exhaust grille..) |  | BK-SUR-ENG-HVC-01-04925 | 2022-06-29 | all data about air distribution devices such as air flow and dimension mentioned in document.
7 | to add general notes inclding : 1-ALL DIMENSIONS ARE IN MILLIMETERS AND ALL ELEVATIONS ARE IN METERS. 2-THE EQUIPMENT SIZE MAY BE CHANGEABLE BY THE LATEST VENDOR DATA. 3-THESE DRAWINGS MUST BE READ IN CONJUNCTION WITH ARCH, STRUCTURAL, ELECTRICAL, INSTRUMENT, HVAC, SAFETY AND ... DRAWINGS. 4-DETAILS OF INDOOR & OUTDOOR UNIT INSTALLATION SHALL BE SUBMITTED AFTER VENDOR FINALIZED. 5-ELEVATION ±0.00 ARE REFEREED TO THE CONVENTIONAL VALUE ??? . |  | BK-SUR-ENG-HVC-01-04925 | 2022-06-29 | noted & done.
8 | detail for refrigeration piping + sleeve through wall / roof shall add (or refer to other details) |  | BK-SUR-ENG-HVC-01-04925 | 2022-06-29 | noted & done.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: K.Ahmadi | Signature | M.Fakharian
| Date: 06/29/2022 |  |  |  |  | Date: 07/26/2023