## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 8
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0007 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
I&C POWER CONSUMPTION SUMMARY نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | AUG.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D02 |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708973
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 8
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0007 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X |  | X |  |  |  | 69
6 |  | X | X |  | X |  |  |  | 70
7 |  |  |  |  | X |  |  |  | 71
8 |  |  |  |  | X |  |  |  | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCES
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 8
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D03
REFERENCE DOCUMENTS:
| I/O LIST FOR CONTROL SYSTM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0002
| I/OLIST FOR ESD SYSTEM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0003
| I/O LIST FOR F&G SYSTEM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0004
| SPECIFICATION FOR INSTRUMENTATION | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| SPECIFICATION FOR CONTROL SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0002
| SPECIFICATION FOR ESD SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0003
| SPECIFICATION FOR ESD SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0012
| SPECIFICATION FOR INSTRUMENT AND CONTROL OF PACKAGE UNIT SYSTEM(PU | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0004

## UPS 110 VAC
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 4 از 8
9184 – 073 - 053 |  |  |  |  | BK | GCS |  | PEDCO |  | 120 |  | IN | LI |  | 0007 |  | D03
INST./CONTROL UPS 110 VAC POWER CONSUMPTION TABLE
- Table (1) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 3) |  |  | POWER CONSUMPTION (W) (Note 1)( AS PER APPENDIX A,B) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION (W)
| 1 | DCS SYSTEM PANEL (AS PER APPENDEX "A") |  | Power Supply for CPUs ( 2 No. redundant) |  | 1 | 2 hr. | 400 |  |  | 500 |  |  | 2 Nos. (Redundant) |  | 1100
|  |  |  | 220/24 VDC Power Supply |  |  | 2 hr. |  |  |  | 400 |  |  | 2 Nos. (Redundant)
|  |  |  | Socket - 110 VAC |  |  | - |  |  |  | 200 |  |  | -
| 2 | DCS MARSHALING PANEL (AS PER APPENDEX "B") |  | 220/24 VDC Power Supply ( 2 No. redundant) |  | 3 | 2 hr. | - |  |  | 700 |  |  | 2 Nos. (Redundant) |  | 900
|  |  |  | Socket - 110 VAC |  |  | - |  |  |  | 200 |  |  | -
| 3 | ESD SYSTEM PANEL (AS PER APPENDEX "A") |  | Power Supply for CPUs ( 2 No. redundant) |  | 1 | 2 hr. | 200 |  |  | 500 |  |  | 2 Nos. (Redundant) |  | 1280
|  |  |  | 220/24 VDC Power Supply |  |  | 2 hr. |  |  |  | 580 |  |  | 2 Nos. (Redundant)
|  |  |  | Socket - 110 VAC |  |  | - |  |  |  | 200 |  |  | -
| 4 | ESD MARSHALING PANEL (AS PER APPENDEX "B") |  | 220/24 VDC Power Supply |  | 2 | 2 hr. | - |  |  | 380 |  |  | 2 Nos. (Redundant) |  | 580
|  |  |  | Socket - 110 VAC |  |  | - |  |  |  | 200 |  |  | -
| 5 | ELECRO GAS COMPRESSOR UCP A/B/C SYSTEM AND MARSHALING CABINET |  |  |  | 3 | 2 hr. | 3x200 |  |  | 1500 |  |  | 2 Nos. (Redundant) |  | 4500
| 6 | DEHYDRATION PACKAGE(UCP/BMS) |  |  |  | 2 | 2 hr. | 20 |  |  | 1500 |  |  | 2 Nos. (Redundant) | 1 | 3000
| 7 | PAGING SYSTEM |  |  |  | 1 | 2 hr. | - |  |  | 1000 |  |  | 2 Nos. (Redundant) | 1 | 1000
| 8 | AIR COMPRESSOR UCP A/B |  |  |  | 2 | 2 hr. | 2x100 |  |  | 1000 |  |  | 2 Nos. (Redundant) | 2 | 2000
| 9 | AIR DRAYER LOCAL LCP |  |  |  | 2 | 2 hr. | - |  |  | 800 |  |  | 2 Nos. (Redundant) | 2 | 1600
| 10 | NITROGEN PACKAGE UCP A/B |  |  |  | 1 | 2 hr. | 100 |  |  | 1000 |  |  | 2 Nos. (Redundant) | 2 | 1000
| 11 | OPERATOR WORKSTATION (INCLUDING DCS, ESD, PACKAGE OWSs) |  |  |  | 4 | 2 hr. | - |  |  | 741 |  |  | 1 No. ( Socket) | 4 | 2964
| 12 | DCS ENGINEERING WORKSTATION |  |  |  | 1 | 2 hr. | - |  |  | 713 |  |  | 1 No. ( Socket) | 4 | 713
| 13 | ESD ENGINEERING WORKSTATION |  |  |  | 1 | 2 hr. | - |  |  | 713 |  |  | 1 No. ( Socket) | 4 | 713
| 14 | F&G OPERATOR/ ENGINEERING WORKSTATION |  |  |  | 1 | 2 hr. | - |  |  | 713 |  |  | 1 No. ( Socket) | 4 | 713
| 15 | PRINTER |  |  |  | 3 | 2 hr. | - |  |  | 600 |  |  | 3 No. ( Socket) | 4 | 1800
TABLE 1
|  |  | TOTAL POWER CONSUMPTION (W) | [12 empty] | 23863
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (W) | [12 empty] | 28635.6
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents.
Note 3: UPS power for HVAC Panel shall be supplied by vendor. Only 400VAC , 3 phase will be supplied by EPC contractor.
Note 3: Power Consumption of panels have been estimatted considering project I/O count. Refer to '' I/O List For Control System Doc.No.BK-GCS-PEDCO-120-IN-LI-0002 , I/O List For ESD System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003
Note 4 : UPS of CCTV panel is not considered.It will be provided by vendor.
D03
D03
D03

## NON UPS 230 VAC
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 8
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN | LI | 0007 | D03
INST./CONTROL NON- UPS 230 VAC POWER CONSUMPTION TABLE
- Table (2) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room.
| ITEM | DESCRIPTION |  |  | UNIT POWER CONSUMPTION (W) (Note 1) | [5 empty] | QTY. (Note 1) | TOTAL POWER CONSUMPTION (W) + 500 W for 1 Socket per system
| 1 | Cabinet Utilities For DCS (Heater, Fan , Light) |  |  | 200 | [5 empty] | 4 | 1300
| 2 | Cabinet Utilities For ESD (Heater, Fan , Light) |  |  | 200 | [5 empty] | 3 | 1100
| 3 | Cabinet Utilities For F&G (Heater, Fan , Light) |  |  | 200 | [5 empty] | 3 | 1100
| 4 | Cabinet Utilities For Gas Compressor UCP(Heater, Fan , Light) |  |  | 200 | [5 empty] | 3 | 1100
| 5 | Cabinet Utilities For Dehydration BMS( if any) (Heater, Socket, Fan , Light) |  |  | 200 | [5 empty] | 1 | 700
| 6 | Cabinet Utilities For Total Flooding UCP(Heater, Socket, Fan , Light) |  |  | 200 | [5 empty] | 1 | 700
| 7 | Cabinet Utilities For Paging Cabinet (Heater, Socket, Fan , Light) |  |  | 200 | [5 empty] | 1 | 700
| 8 | Cabinet Utilities For Air Compressor UCP(Heater, Socket, Fan , Light) |  |  | 200 | [5 empty] | 2 | 900
| 9 | Cabinet Utilities For Nitrogen package UCP(Heater, Socket, Fan , Light) |  |  | 200 | [5 empty] | 2 | 900
| 10 | Control Desk Sockets |  |  | 500 | [5 empty] | 7 | 3500
| TOTAL POWER CONSUMPTION | [10 empty] | 12000
TABLE 2
|  |  | TOTAL POWER CONSUMPTION (W) | [8 empty] | 12000
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (W) | [8 empty] | 14400
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents.
D03
D03
D03

## 24 VDC CHARGER
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 6 از 8
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 |  | IN | LI |  | 0007 |  | D03
INST./CONTROL UPS 24 VDC POWER CONSUMPTION TABLE
- Table (3) is represents 24V DC UPS power consumption for F&G system. The estimation is based on the design of F&G systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 4) |  | POWER CONSUMPTION (W) ( Refer to appendix A,B) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION FOR QUIESENCE MODE(W) (Note 3) |  |  | TOTAL POWER CONSUMPTION FOR ALARM MODE (W) (Note 3)
| 1 | F&G SYSTEM PANEL |  |  | 1 | 24hr. | 265 |  | 1400 |  |  | 2 Nos. (Redundant) |  | 1600 |  |  | 2700
( for Quiescence- Refer to appendix A)
[6 empty] | 5 MIN |  |  | 2500
(for alarm mode- Refer to appendix A)
| 2 | F&G MARSHALLING PANEL |  |  | 2 | 24hr. |  |  | 200
( for Quiescence- Refer to appendix B)
| 1 | FACP system |  |  | 1 | 24hr. | - |  | 400 ( for Quiescence) |  |  | 2 Nos. (Redundant) |  | 540 |  |  | -
| 2 | FACP Detectors |  |  |  | 24hr. |  |  | 140 (for Quiescence mode)
[6 empty] | 5 MIN |  |  | 500 (for alarm mode) |  |  |  |  | - |  |  | 900
| 3 | FIRE PROTECTION AND TOTAL FLOODING SYSTEM UCP |  |  | 1 | 5 MIN | 50 |  | 800 |  |  | 2 Nos. (Redundant) | 2 | - |  |  | 800
|  |  | TOTAL POWER CONSUMPTION FOR 5 MIN BACK UP TIME (W) (Note 3) | [10 empty] | 4400
|  |  | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME (W) (Note 3) | [10 empty] | 2140
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITYFOR 5 MIN BACK UP TIME (W) | [10 empty] | 5280
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY FOR 24 HOURS BACK UP TIME (W) | [10 empty] | 2568
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Note 2: Deleted Note 3: DC charger shall supply 2KW + Spare, for 24H back up time but also it shall be capable to prepare 4.3KW+ Spare, as a peak power consumption in alarming conditions for 5 Min back up time. it shall be considered during battery sizing in related documents. Note 4: Power Consumption of panels have been estimatted considering project I/O count. Refer to '' I/O List For Control System Doc.No.BK-GCS-PEDCO-120-IN-LI-0002 , I/O List For ESD System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003.
D03
D03
D03
D03
D03
D03

## (APPENDIX A)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 7 از 8
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 |  | D03
(APPENDIX "A")
| ITEM | DESCRIPTION |  |  |  | QTY |  | UNIT POWER CONSUMPTION (W) (Note 1)( 1.5 contingency) |  |  |  | TOTAL POWER CONSUMPTION (W)
| 1 | DCS SYSTEM PANEL (As per last DCS I/O List) |  | Interface Base Plates |  | 8 |  | 8.25 |  |  |  | 66
| 2 |  |  | Commuication Processor Module |  | 7 |  | 3.6 |  |  |  | 25.2
| 3 | DI-NR : | 192 | DI Module 32 Channel |  | 8 |  | 5.25 |  |  |  | 42 |  |  |  |  | DI-NR | 192 | 7.68 | 8 | - | -
| 4 | DO-NR : | 69 | DO Module 32 Channel |  | 5 |  | 10.2 |  |  |  | 51 |  |  |  |  | DO-NR | 69 | 2.76 | 3 | DO-R | 2 | 1 | 1
| 5 | DO-R : | 2 | AI Module 16 Channel |  | 11 |  | 2.25 |  |  |  | 24.75 |  |  |  |  | AI-NR | 33 | 2.75 | 3 | AI-R | 46 | 3.8333 | 4
| 6 | AI-NR : | 33 | AO Module 8 Channel |  | 8 |  | 9 |  |  |  | 72 |  |  |  |  | AO-R | 23 | 3.8333 | 4 | - | -
| 7 | AI-R : | 46 | Industrial Ethernet Switch |  | 2 |  | 22.5 |  |  |  | 45
| 8 | AO-R : | 23 | Spare |  | 1 SET |  | 70 |  |  |  | 70
[8 empty] | TOTAL : |  |  |  | 395.95
| ITEM | DESCRIPTION |  |  |  | QTY |  | UNIT POWER CONSUMPTION (W) (Note 1)( 1.5 contingency) |  |  |  | TOTAL POWER CONSUMPTION (W)
| 1 | ESD SYSTEM PANEL (As per last DCS I/O List) |  | Interface Base Plates |  | 8 |  | 8.25 |  |  |  | 66
| 2 |  |  | DI Module 24 Channel |  | 4 |  | 15 |  |  |  | 60 |  |  |  |  | DI-R | 39 | 1.95 | 2
| 3 | DI-R : | 39 | DO Module 10 Channel |  | 24 |  | 9 |  |  |  | 216 |  |  |  |  | DO-R | 91 | 11.375 | 12
| 4 | DO-R : | 91 | AI Module 6 Channel |  | 24 |  | 6.75 |  |  |  | 162 |  |  |  |  | AI-R | 59 | 11.8 | 12
| 5 | AI-R : | 59 | Spare |  | 1 SET. |  | 70 |  |  |  | 70
[8 empty] | TOTAL : |  |  |  | 574
| ITEM | PANEL NAME |  | DETECTOR TYPE | 24H / 5 MIN | QTY |  | UNIT POWER CONSUMPTION (W) (Note 1)( 1.5 contingency) |  |  |  | TOTAL POWER CONSUMPTION FOR 24H (W) |  |  | TOTAL POWER CONSUMPTION FOR 5 MIN (W)
| 1 |  |  | Flame Detector : | 24H | 19 |  | 1 |  |  |  | 19 |  |  | 0
|  | F&G SYSTEM PANEL 24VDC (External) For field |  | Flame Detector : | 5 MIN | 19 |  | 8 |  |  |  | 0 |  |  | 152 | Flammable Gas Detector-ir | AI-R |  | 33 | 1 | 33
| 2 |  |  | Flammable Gas Detector : | 24H | 33 |  | 1 |  |  |  | 33 |  |  | 0 | Hydrogen Gas Detector | AI-R |  | 3 | 1 | 3
| 2 |  |  | Flammable Gas Detector : | 5 MIN | 33 |  | 13 |  |  |  | 0 |  |  | 429 | Hydrogen Gas Detector | AI-R |  | 3 | 1 | 3
| 3 |  |  | Toxic Gas Detector : | 24H | 33 |  | 1 |  |  |  | 33 |  |  | 0 | Toxic Gas Detector | AI-R |  | 33 | 30 | 990
| 3 |  |  | Toxic Gas Detector : | 5 MIN | 33 |  | 13 |  |  |  | 0 |  |  | 429 | Toxic Gas Detector | AI-R |  | 33 | 30 | 990
| 4 |  |  | Hydrogen Gas Detector : | 24H | 3 |  | 1 |  |  |  | 3 |  |  | 0
| 4 |  |  | Hydrogen Gas Detector : | 5 MIN | 3 |  | 13 |  |  |  | 0 |  |  | 39
| 5 |  |  | Manual Call Point : | 24H | 19 |  | 0 |  |  |  | 0 |  |  | 0
| 6 |  |  | Heat Detector : | 24H | 3 |  | 3 |  |  |  | 9 |  |  | 0
| 7 |  |  | Linear Heat Detector : | 24H | 4 |  | 4.2 |  |  |  | 16.8 |  |  | 0
| 8 |  |  | Beacon : | 5 MIN | 30 |  | 1 |  |  |  | 0 |  |  | 30
| 9 |  |  | Horn : | 5 MIN | 10 |  | 6 |  |  |  | 0 |  |  | 60
| 1 | F&G SYSTEM PANEL (As per last F&G I/O List) 24VDC (Internal) |  | CPU | 24H/5 MIN | 2 |  | 285 |  |  |  | 570 |  |  | 570
| 2 |  |  | DI Module 24 Channel | 24H/5 MIN | 6 |  | 15 |  |  |  | 90 |  |  | 90
| 3 | AI-R : | 88 | DO Module 10 Channel | 24H/5 MIN | 34 |  | 9 |  |  |  | 306 |  |  | 306
| 4 | DI-NR : | 47 | AI Module 6 Channel | 24H/5 MIN | 36 |  | 6.75 |  |  |  | 243 |  |  | 243
| 5 | DO-NR : | 130 | Spare | 24H/5 MIN | 1 |  | 72 |  |  |  | 72 |  |  | 72
[6 empty] | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME : | [5 empty] | 1394.8
[6 empty] | TOTAL POWER CONSUMPTION FOR 5 MIN BACK UP TIME : | [8 empty] | 2420
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. ( As per Siemens base )
D03

## (APPENDIX B)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 8 از 8
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 |  | D03
(APPENDIX "B")
| ITEM | DESCRIPTION |  |  | QTY |  | UNIT POWER CONSUMPTION (W) (Note 1)( 1.5 contingency) |  |  |  | TOTAL POWER CONSUMPTION (W)
| 1 | DCS MARSHALING PANEL | Barrier |  | 123 |  | 2.55 |  |  |  | 313.65
| 2 |  | Relay Coils |  | 315 |  | 1 |  |  |  | 315
| 3 |  | Spare |  | 1 SET |  | 70 |  |  |  | 70
[7 empty] | TOTAL : |  |  |  | 698.65
| 1 | ESD MARSHALING PANEL | Barrier |  | 59 |  | 2.55 |  |  |  | 150.45
| 2 |  | Relay Coils |  | 156 |  | 1 |  |  |  | 156
| 3 |  | Spare |  | 1 SET |  | 70 |  |  |  | 70
[7 empty] | TOTAL : |  |  |  | 376.45
| 1 | F&G MARSHALING PANEL | Relay Coils |  | 130 |  | 1 |  |  |  | 130
| 2 |  | Spare |  | 1 SET |  | 70 |  |  |  | 70
[5 empty] | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME : | [5 empty] | 200
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. ( As per Siemens base )
D03