| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CALCULATION NOTE FOR LIGHTING SYSTEM OF WELL PADS AREA نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D04 | Aug. 2023 | IFA | H.Shakiba | M.Fakharian | A.M.Mohseni |  |
| D03 | Nov. 2022 | IFA | H.Shakiba | M.Fakharian | M.Mehrshad |  |
| D02 | Oct. 2022 | IFA | H.Shakiba | M.Fakharian | M.Mehrshad |  |
| D01 | Jul. 2022 | IFA | H.Shakiba | M.Fakharian | M.Mehrshad |  |
| D00 | May. 2022 | IFC | H.Shakiba | M.Fakharian | M.Mehrshad |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | Client Approval |
| Class:2 |  | Client Doc. Number: F0Z-707380 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X | X | X |  | 51 |  |  |  |  |  |
| 2 | X | X | X | X | X |  | 52 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 53 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 54 |  |  |  |  |  |
| 5 | X | X |  | X | X |  | 55 |  |  |  |  |  |
| 6 | X | X |  | X |  |  | 56 |  |  |  |  |  |
| 7 | X |  |  | X |  |  | 57 |  |  |  |  |  |
| 8 | X |  |  | X |  |  | 58 |  |  |  |  |  |
| 9 |  |  |  |  |  |  | 59 |  |  |  |  |  |
| 10 |  |  |  |  |  |  | 60 |  |  |  |  |  |
| 11 |  |  |  |  |  |  | 61 |  |  |  |  |  |
| 12 |  |  |  |  |  |  | 62 |  |  |  |  |  |
| 13 |  |  |  |  |  |  | 63 |  |  |  |  |  |
| 14 |  |  |  |  |  |  | 64 |  |  |  |  |  |
| 15 |  |  |  |  |  |  | 65 |  |  |  |  |  |
| 16 |  |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 |  |  |  |  |  |  | 68 |  |  |  |  |  |
| 19 |  |  |  |  |  |  | 69 |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	5

3.0	NORMATIVE REFERENCES	5

3.1	Codes and Standards	5

3.2	The Project reference  Documents	5

4.0	LANGUAGE AND SYSTEM OF UNITS	5

5.0	Lighting system	5

6.0	Design software	8

7.0	LIGHTING CALCULATION – dETAIL REPORT	8

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – General Facilities |
| EPD/EPC CONTRACTOR(GC) | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection(D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR(GC) and approved by COMPANY (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- Scope

This specification describes the practices that shall be employed and the Standards that will be required to be met for the Area Lightings Illumination

- NORMATIVE REFERENCES

  - Codes and Standards

- IPS-E-EL-100	Engineering Standard For Electrical System Design (Industrial And Non-Industrial)

  - The Project reference  Documents

- BK-GNRAL-PEDCO-000-PR-DB-0001	Process Basis Of Design

- BK-GNRAL-PEDCO-000-EL-DC-0001	Electrical System Design Criteria

D04

BK-GNRAL-PEDCO-000-EL-SP-0007	Specification For Lighting & Small Power   System

- BK-W046S-PEDCO-110-PI-DW-0001		Plot Plan Drawing - W046S

- BK-W007S-PEDCO-110-PI-PY-0002		Plot Plan Drawing - W007S

- BK-BK14-PEDCO-110-PI-PY-0001		Plot Plan Drawing – BK14

- BK-BK12-PEDCO-110-PI-PY-0001		Plot Plan Drawing – BK12

- BK-BK15-PEDCO-110-PI-PY-0001		Plot Plan Drawing – BK15

- BK-BK05-PEDCO-110-PI-PY-0001		Plot Plan Drawing – BK05

- BK-W046S-PEDCO-110-SA-PY-0001		Hazardous Area Classification W046S

- LANGUAGE AND SYSTEM OF UNITS

All documentation, drawings, data, etc. furnished by the manufacturer shall be in English. SI metric system of measurement shall be used except for pipe and pipe fitting sizes, flange ratings and nozzle dimensions in which inch will be used.

- Lighting system

The lighting system will provide a uniform and adequate light distribution in all working areas, the minimum average illumination levels will be as per IPS-E-EL-100(1). Major areas indicated in the below table:

| Comparison of Lighting Between Standard & Calculation (LUX) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Outdoor Area | Standard | Calculation (Av) With 4 Metal Halid 400 W | Calculation (Av) With 6 Metal Halid 400 W | Calculation (Av) With 6 LED 200 W |
| 1 | General Area | 10 | 10< | 14 | 13 |

According to above table there is not more different between 4 metal halid & 6 metal halid & 6 LED in lux. Therefore according to basic document, 4 metal halid in each lattice 15 m tower will be considered in layout.

- Design software

Calculation is performed with version 4.13 of DIALUX Software.

- LIGHTING CALCULATION – dETAIL REPORT

DIALUX report has been attached in “Attachment”