## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DT-0005_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1335 |  |  | Transmital Date: 8/28/2022
Document Title: Data Sheets For ON/OFF & Shutdown Valves - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1335 |  |  | Transmital Date: 8/28/2022
[5 empty] | CRS No: BK-W007S-PEDCO-110-IN-DT-0005_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-02-07865 | 2023-06-13 | ملاحظه شد.
2 | با توجه به اينكه مدرك داراي كامنت بوده و به كارفرما ارسال نشده است لطفا اين مدرك با در نظر گرفتن كامنت هاي زير در همين نسخه مجددا ارائه گردد. |  | BK-SUR-ENG-INS-02-07865 | 2023-06-13 | اعمال شد.
3 | Air Compressor Design Pressure موجود به وندور اعلام گردد و وندور تمهيدات لازم براي اين منظور را در نظر بگيرد. |  | BK-SUR-ENG-INS-02-07865 | 2023-06-13 | اعمال شد. در نوت ۱۵ اضافه شد.
4 | 1- با توجه به كلاس خط (LN15) در ديتاشيت ها بايستي براي شيرهاي مذكور مطابق PMS پروژه به استاندارد API 6A اشاره گردد. 2- براي شيرهاي مذكور در ديتاشيت بايستي مطابق PMS پروژه و استاندارد API 6A اشاره گردد كه متريال بر اساس Material Class EE مي باشد. لازم به ذكر است نقطه نظرات فوق در ويرايش قبلي مدرك نيز ذكر گرديده بود و پاسخ پيمانكار در CRS ارسالي قابل پذيرش نمي باشد. |  | BK-SUR-ENG-INS-02-07865 | 2023-06-13 | اعمال شد.
5 | در خصوص متريال، ضمن تاييد اينكه PMS مرجع اصلي متريال مي باشد جزئيات آن مشابه با مدرك Manual Valve ارائه و مشخص شود. |  | BK-SUR-ENG-INS-02-07865 | 2023-06-13 | رجوع به PMS درمدرک اورده شده است.مدرک مطابق شیر BALL درجدول LN15 و مدرک Specification شیر در بخش ابزار دقیق تکمیل شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 13 Jun 2023 |  |  |  |  | Date: