## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0002 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR TEMPERATURE GAUGE نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | AUG.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  | JUL.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | Client Approval
Class:1 |  |  |  | Client Doc. Number: F9Z-708923
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for Client Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0002 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X | [5 empty] | 70
7 |  | X | X | [5 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0002 | D02
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## NOTES
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 7
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0002 | D02
GENERAL NOTES:
1- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
2- 304 SS (VTC) name plate shall be supplied for all instruments specified in this document. Following details shall be engraved on them:
• Tag Number • Range Limit • Manufacture Model
3- Environmental Condition For Field Instrumentation Of BINAK Complex Shall Be Considered As Per The Following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
4- Temperature gauges shall be fully adjustable type (Every Angle).
5- Temperature gauges shall be double scale type (°C and °F).
6 - Material Test Certificate and calibration Certificate for all gauges to be submitted by Vendor.
7 - All lines below 4", shall be expanded to 4" to be suitable for thermowell installation.
8- Temperature elements shall be capable of withstanding intermittent over-ranging to 1.5 times the maximum scale.
9- Pipe Nozzle projection length in GCS /Manifold / Pipeline as 162 mm.
10-For Wellhead area and all vessel connection 200 mm.
D02

## TG
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 5 از 7
9184 – 073 - 053 |  |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0002 |  | D02
TEMPERATURE GAUGE
| GENERAL DATA |  | 1 | Tag No. |  |  |  | Service | [5 empty] | SEE PAGE 6
|  |  | 2 | P&ID |  |  |  | Line No./Equipment No. | [5 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 3 | Piping Class |  |  |  | Schedule | [5 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 4 | Line Size | [9 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 5 | Area Clacification |  |  |  | Phase | [5 empty] | ZONE 2, IIB T4
| PROCESS CONDITION |  | 6 | Fluid |  |  |  | Design Temperature | [5 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 7 | Operating Temperature |  |  |  | Design Pressure |  |  |  | (°C) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 8 | Operating Pressure | [7 empty] | (barg) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 9 | Density |  |  |  | Viscosity (Liquid) |  |  |  | (Kg/m3) |  | SEE PAGE 6
|  |  | 10 | Viscosity (Vapor) |  |  |  | Velocity (Liquid) |  |  |  | (C.P) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 11 | Velocity (Vapor) | [7 empty] | (m/s) |  | VTA |  |  | VTA
| THERMOMETER |  | 12 | Type | [9 empty] | Bimetal-Every Angle
|  |  | 13 | Instrument Range | [9 empty] | SEE PAGE 6
|  |  | 14 | Dial Size |  |  |  | Dial Color | [5 empty] | 150 mm |  |  | Black figures on white dial.
|  |  | 15 | Case Material |  |  |  | Dial Material | [5 empty] | SS 304 |  |  | Aluminium
|  |  | 16 | Stem Material |  |  |  | Window | [5 empty] | 316 SS |  |  | (Note 1)
|  |  | 17 | Stem Adjustable Union | [9 empty] | Required
|  |  | 18 | Stem Position | [9 empty] | Bottom
|  |  | 19 | Stem Length | [9 empty] | Suit for Well (VTA) (Note 4)
|  |  | 20 | Stem Diameter | [9 empty] | 6 mm
|  |  | 21 | Accuracy | [9 empty] | ±1% of F.S
|  |  | 22 | Weather Protection | [9 empty] | IP-65 as minimum-Hermitically sealed
|  |  | 23 | Zero Adjustement | [9 empty] | Local
| THERMOWELL (Note 2,3) |  | 24 | Construction Type | [9 empty] | Drilled Solid Bar Stock in Tapered Configuration
|  |  | 25 | Element Connection | [9 empty] | 1/2 " NPTF
|  |  | 26 | Size (in) |  |  |  | Rating (lbs) | [5 empty] | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 27 | Process Connection | [9 empty] | Flanged |  |  | SEE PAGE 6
|  |  | 28 | Flange Facing | [9 empty] | SEE PAGE 6
|  |  | 29 | Insertion Length(U) | [7 empty] | (mm) |  | SEE PAGE 6
|  |  | 30 | LAG Extension (T) | [7 empty] | (mm) |  | N/A
|  |  | 31 | Flange Material | [9 empty] | S.S 316L
|  |  | 32 | Well Material | [9 empty] | S.S 316L
|  |  | 33 | NACE Requirements (NACE MR-0175/ISO 15156) | [9 empty] | SEE PAGE 6
|  |  | 37 | Wake Frequency Standard | [9 empty] | Required as per ASME PTC 19.3
| PURCHASING DATA |  | 38 | Model |  |  |  | Manufacturer | [5 empty] | Note 8 |  |  | Note 8
|  |  | 39 | Supplier |  |  |  | Order | [5 empty] | Note 8 |  |  | Note 8
40
NOTES :
|  | VTA : VENDOR TO ADVISE |  |  |  |  | N/A: NOT APPLICABLE
(1) Window shall be heavy plate glass, breakage resistance and shatter proof.
(2) Thermowell wake frequency analysis (stress calculation) according to ASME Power Test Code 19.3 shall be done & submitted by vendor.
(3) Well length must suit for stem length.
(4) According to thermowell dimension, suitable length should be provided for thermometer stem.
(5) Temperature gauges shall be fully adjustable type (Every Angle).
(6) Temperature gauges shall be double scale type (°C and °F).
(7) NACE requirement to be as per MR-0175/ISO 15156 if mentioned in data sheet.
(8) Will be finalized later at the purchasing time.
(9) Area classification for all tags to be Zone 2, IIB T4

## TG LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR TEMPERATURE GAUGE
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | IN |  | DT |  | 0002 |  | D02
TEMPERATURE GAUGE
Rev. | Item No. | Tag No. | P&ID No. | Piping Class | Line No./Equipment No. |  | SERVICE |  | Line Size/ Flange Facing/ Sch |  | Fluid |  | Phase | Operating Temprature (°C) | Design Temprature (°C) | Operating Pressure (barg) | Design Pressure (barg) | Density (Kg/m3) (vapour/LIQUID/Mixed) | Viscosity (CP) (vapour/LIQUID/water) | Velocity(m/s) | Actual Vol. Flow (m3/h) (Gas/ Oil/ Water) | Instrument Range (°C) | Process Connection Size(in) | Rating | Insertion Length (U) mm | NACE | Remark
| 1 | TG-2111 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | AN07 | V-2104 |  | SLUG CATCHER DRUM |  | - |  | HYDROCARBON / GAS |  | GAS | 15.5-32 | 85 | 5.5 | FV/9 | 6.21 | 0.011446 | 0.36 | - | 0-100 | 2" | 300 | 500 | Yes
| 2 | TG-2112A | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | CN05 | CDH-112-0012-CN05-3"-PT |  | SLUG PUMP P-2101A DISCHARGE LINE |  | 3" / 300/RF SCH.40 |  | HYDROCARBON / LIQUID |  | LIQUID | AMB | 85 | 19.5 | 47.7 | - /676.2/726.76 | - / 0.39 / 0.66 | 0.64 | - | 0-100 | 1 1/2" | 300 | 200 (NOTE 7 IN GENERAL NOTES) | Yes
| 3 | TG-2112B | BK-GCS-PEDCO-120-PR-PI-0004 (2 of2) | CN05 | CDH-112-0013-CN05-3"-PT |  | SLUG PUMP P-2101B DISCHARGE LINE |  | 3" / 300/RF SCH.40 |  | HYDROCARBON / LIQUID |  | LIQUID | AMB | 85 | 19.5 | 47.7 | - /676.2/726.76 | - / 0.39 / 0.66 | 0.64 | - | 0-100 | 1 1/2" | 300 | 200 (NOTE 7 IN GENERAL NOTES) | Yes
| 4 | TG-2113 | BK-GCS-PEDCO-120-PR-PI-0005 | - | V-2105 |  | INLET KNOCK OUT DRUM |  | - |  | HYDROCARBON / GAS |  | GAS | 19-37 | 85 | 5.3 | FV/9 | 6.165 /648.6/ 998.22 | 0.01 / - / 0.688 | 1.38 | - | 0-100 | 2" | 300 | 500 | Yes
| 5 | TG-2114 | BK-GCS-PEDCO-120-PR-PI-0005 | AN07 | GAS-111-0025-AN07-10"-PT |  | 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD |  | 10" / 150/RF / SCH.40 |  | HYDROCARBON / GAS |  | GAS | 19-37 | 85 | 5.3 | 18.2 | 5.97 | 0.011485 | 16.31 | - | 0-100 | 1 1/2" | 300 | 300 | Yes
| 6 | TG-2121A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | - | V-2101-A |  | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #A |  | - |  | HYDROCARBON / GAS |  | GAS | 19-37 | 85 | 5.1 | FV/22 | 5.9689 | 0.011485 | 31.7 | - | 0-100 | 2" | 300 | 500 | Yes
| 7 | TG-2121B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | - | V-2101-B |  | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #B |  | - |  | HYDROCARBON / GAS |  | GAS | 19-37 | 85 | 5.1 | FV/22 | 5.9689 | 0.011485 | 31.7 | - | 0-100 | 2" | 300 | 500 | Yes
| 8 | TG-2121C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | - | V-2101-C |  | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #C |  | - |  | HYDROCARBON / GAS |  | GAS | 19-37 | 85 | 5.1 | FV/22 | 5.9689 | 0.011485 | 31.7 | - | 0-100 | 2" | 300 | 500 | Yes
| 9 | TG-2122A | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | AN05 | GAS-111-0031A-CN05-8"-ET |  | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101A) TO C-2101-A |  | 8" / 300/RF / SCH.40 |  | HYDROCARBON / GAS |  | GAS | 18-35 | 85 | 4.9 | 47.7 | 5.77/ - / 842.66 | 0.01 / - / 0.693 | 12.92 | - | 0-100 | 1 1/2" | 300 | 300 | Yes
| 10 | TG-2123A | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | CN05 | GAS-111-0036A-CN05-6"-NP |  | OUTLET COMP. C-2101-A / TO 1ST STAGE AIR COOLER (AE-2101A) |  | 6" / 300/RF SCH.40 |  | HYDROCARBON / GAS |  | GAS | 113/125 | 155 | 19 | 47.7 | 15.3834 | 0.014761 | 8.4 | - | 0-250 | 1 1/2" | 300 | 250 | Yes
| 11 | TG-2122B | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | AN05 | GAS-111-0031B-CN05-8"-ET |  | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101B) TO C-2101-B |  | 8" / 300/RF / SCH.40 |  | HYDROCARBON / GAS |  | GAS | 18-35 | 85 | 4.9 | 47.7 | 5.77/ - / 842.66 | 0.01 / - / 0.693 | 12.92 | - | 0-100 | 1 1/2" | 300 | 300 | Yes
| 12 | TG-2123B | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | CN05 | GAS-111-0036B-CN05-6"-NP |  | OUTLET COMP. C-2101-B / TO 1ST STAGE AIR COOLER (AE-2101B) |  | 6" / 300/RF SCH.40 |  | HYDROCARBON / GAS |  | GAS | 113/125 | 155 | 19 | 47.7 | 15.3834 | 0.014761 | 8.4 | - | 0-250 | 1 1/2" | 300 | 250 | Yes
| 13 | TG-2122C | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | AN05 | GAS-111-0031C-CN05-8"-ET |  | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101C) TO C-2101-C |  | 8" / 300/RF / SCH.40 |  | HYDROCARBON / GAS |  | GAS | 18-35 | 85 | 4.9 | 47.7 | 5.77/ - / 842.66 | 0.01 / - / 0.693 | 12.92 | - | 0-100 | 1 1/2" | 300 | 300 | Yes
| 14 | TG-2123C | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | CN05 | GAS-111-0036C-CN05-6"-NP |  | OUTLET COMP. C-2101-C / TO 1ST STAGE AIR COOLER (AE-2101C) |  | 6" / 300/RF SCH.40 |  | HYDROCARBON / GAS |  | GAS | 113/125 | 155 | 19 | 47.7 | 15.3834 | 0.014761 | 8.4 | - | 0-250 | 1 1/2" | 300 | 250 | Yes
| 15 | TG-2124A | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) | CS00 | GAS-111-0037A-CS00-6"-NP |  | FROM 1ST STAGE GAS COMPRESSOR AIR COOLERS (AE-2101-A) |  | 6" / 300/RF / SCH.10S |  | HYDROCARBON / GAS |  | GAS / LIQUID | 60 | 155 | 18.3 | 30.3 | 18.28 | 0.012653 | 7.06 | - | 0-160 | 1 1/2" | 300 | 250 | No
| 16 | TG-2124B | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) | CS00 | GAS-111-0037B-CS00-6"-NP |  | FROM 1ST STAGE GAS COMPRESSOR AIR COOLERS (AE-2101-B) |  | 6" / 300/RF / SCH.10S |  | HYDROCARBON / GAS |  | GAS / LIQUID | 60 | 155 | 18.3 | 30.3 | 18.28 | 0.012653 | 7.06 | - | 0-160 | 1 1/2" | 300 | 250 | No
| 17 | TG-2124C | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) | CS00 | GAS-111-0037C-CS00-6"-NP |  | FROM 1ST STAGE GAS COMPRESSOR AIR COOLERS (AE-2101-C) |  | 6" / 300/RF / SCH.10S |  | HYDROCARBON / GAS |  | GAS / LIQUID | 60 | 155 | 18.3 | 30.3 | 18.28 | 0.012653 | 7.06 | - | 0-160 | 1 1/2" | 300 | 250 | No
| 18 | TG-2131A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | - | V-2102-A |  | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #A |  | - |  | HYDROCARBON / GAS |  | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.2771 | 0.012653 | 18.1 | - | 0-160 | 2" | 300 | 500 | Yes
| 19 | TG-2131B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | - | V-2102-B |  | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #B |  | - |  | HYDROCARBON / GAS |  | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.2771 | 0.012653 | 18.1 | - | 0-160 | 2" | 300 | 500 | Yes
| 20 | TG-2131C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | - | V-2102-C |  | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #C |  | - |  | HYDROCARBON / GAS |  | GAS | 60 | 115.4 | 18.3 | FV/22 | 18.2771 | 0.012653 | 18.1 | - | 0-160 | 2" | 300 | 500 | Yes
| 21 | TG-2132A | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | CN05 | GAS-111-0044A-CN05-6"-ET |  | 2ND STAGE GAS COMPRESSOR TRAIN #A SUCTION LINE |  | 6" / 300/RF SCH.40 |  | HYDROCARBON / GAS |  | GAS | 59-60 | 115.4 | 18.1 | 47.7 | 18.08 | 0.012642 | 7.14 | - | 0-160 | 1 1/2" | 300 | 250 | Yes
| 22 | TG-2133A | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | FN05 | GAS-111-0051A-FN05-6"-IS |  | 2ND STAGE GAS COMPRESSOR TRAIN #A DISCHARGE LINE |  | 6" / 600/RF /SCH.80 |  | HYDROCARBON / GAS |  | GAS | 142-150 | 175 | 54.8 | 90 | 18.28 | 0.012653 | 3.008 | - | 0-250 | 1 1/2" | 600 | 250 | Yes
| 23 | TG-2132B | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | CN05 | GAS-111-0044B-CN05-6"-ET |  | 2ND STAGE GAS COMPRESSOR TRAIN #B SUCTION LINE |  | 6" / 300/RF SCH.40 |  | HYDROCARBON / GAS |  | GAS | 59-60 | 115.4 | 18.1 | 47.7 | 18.08 | 0.012642 | 7.14 | - | 0-160 | 1 1/2" | 300 | 250 | Yes
| 24 | TG-2133B | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | FN05 | GAS-111-0051B-FN05-6"-IS |  | 2ND STAGE GAS COMPRESSOR TRAIN #B DISCHARGE LINE |  | 6" / 600/RF /SCH.80 |  | HYDROCARBON / GAS |  | GAS | 142-150 | 175 | 54.8 | 90 | 18.28 | 0.012653 | 3.008 | - | 0-250 | 1 1/2" | 600 | 250 | Yes
| 25 | TG-2132C | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | CN05 | GAS-111-0044C-CN05-6"-ET |  | 2ND STAGE GAS COMPRESSOR TRAIN #C SUCTION LINE |  | 6" / 300/RF SCH.40 |  | HYDROCARBON / GAS |  | GAS | 59-60 | 115.4 | 18.1 | 47.7 | 18.08 | 0.012642 | 7.14 | - | 0-160 | 1 1/2" | 300 | 250 | Yes
| 26 | TG-2133C | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | FN05 | GAS-111-0051C-FN05-6"-IS |  | 2ND STAGE GAS COMPRESSOR TRAIN #C DISCHARGE LINE |  | 6" / 600/RF /SCH.80 |  | HYDROCARBON / GAS |  | GAS | 142-150 | 175 | 54.8 | 90 | 18.28 | 0.012653 | 3.008 | - | 0-250 | 1 1/2" | 600 | 250 | Yes
| 27 | TG-2134A | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | FS00 | GAS-111-0058A-FS00-6"-NP |  | AE-2102A 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN #A OUTLET |  | 6" / 600/RF / SCH.40S |  | HYDROCARBON / GAS |  | GAS / LIQUID | 60 | 175 | 54.1 | 62.4 | 59.39 /-/ 981.9 | 0.01417 /-/ 0.4943 | 2.16 | - | 0-160 | 1 1/2" | 600 | 250 | No
| 28 | TG-2134B | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | FS00 | GAS-111-0058B-FS00-6"-NP |  | AE-2102B 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN #B OUTLET |  | 6" / 600/RF / SCH.40S |  | HYDROCARBON / GAS |  | GAS / LIQUID | 60 | 175 | 54.1 | 62.4 | 59.39 /-/ 981.9 | 0.01417 /-/ 0.4943 | 2.16 | - | 0-160 | 1 1/2" | 600 | 250 | No
| 29 | TG-2134C | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | FS00 | GAS-111-0058C-FS00-6"-NP |  | AE-2102C 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN #C OUTLET |  | 6" / 600/RF / SCH.40S |  | HYDROCARBON / GAS |  | GAS / LIQUID | 60 | 175 | 54.1 | 62.4 | 59.39 /-/ 981.9 | 0.01417 /-/ 0.4943 | 2.16 | - | 0-160 | 1 1/2" | 600 | 250 | No
| 30 | TG-2142 | BK-GCS-PEDCO-120-PR-PI-0012 | FN05 | GAS-111-0066-FN05-6"-PT |  | GAS COMPRESSION DISCHARGE DRUM |  | 6" / 600/RF /SCH.80 |  | HYDROCARBON / GAS |  | GAS | 59-60 | 130 | 53.9 | 90 | 59.17 | 0.014156 | 4.34 | - | 0-160 | 1 1/2" | 600 | 250 | Yes
| 31 | TG-2141 | BK-GCS-PEDCO-120-PR-PI-0012 | - | V-2103 |  | GAS COMPRESSION DISCHARGE DRUM |  | - |  | HYDROCARBON / GAS |  | GAS/LIQUED | 59-60 | 130 | 53.9 | FV/62 | 59.3914 | 0.01/ - /0.49 | 10 | - | 0-160 | 2" | 600 | 500 | Yes
DELETED | 32 | TG-2143 | BK-GCS-PEDCO-120-PR-PI-0012 | FN05 | GAS-111-0066-FN05-6"-PT |  | EQUALIZER LINE INTO DEHYDRATION PACKAGE |  | 6" / 600/RF /SCH.80 |  | HYDROCARBON / GAS |  | GAS | 59-60 | 130 | 53.9 | 62 | 59.17 | 0.014156 | 4.34 | - | 0-160 | 1 1/2" | 600 | 250 | Yes
| 33 | TG-2161 | BK-GCS-PEDCO-120-PR-PI-0014 | AN04 | TEG-111-0001-AN04-3"-PT |  | LEAN GLYCOL STORAGE TANK TO DEHYDRATION PACKAGE |  | 3" / 150/RF / SCH.40 |  | LEAN GLYCOL | Lean Glycol | LIQUID | 30 | 85 | 2.1 | 18.2 | 1100 | 6.63 | 0.32 | - | 0-100 | 1 1/2" | 300 | 200 (NOTE 7 IN GENERAL NOTES) | No
| 34 | TG-2221 | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | AN07 | FLG-112-0010-AN07-2"-PT |  | CLOSED DRAIN DRUM |  | 2" / 150/RF / SCH.160 |  | HYDROCARBON / LIQUID | HYDROCARBON/WATER | LIQUID | AMB | 85 | 0.5 | FV/6 | 980 | 0.45 | N.N.F | - | 0-100 | 1 1/2" | 300 | 200 (NOTE 7 IN GENERAL NOTES) | Yes
| 35 | TG-2251 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) | - | V-2201 |  | LP FLARE K.O. DRUM |  | - |  | FLARE / GAS | HYDROCARBON | GAS | 32 | 85 | 0.5 | FV/6 | 844.4 | 0.73 | 11.55 | - | 0-100 | 2" | 300 | 500 | Yes
| 36 | TG-2271 | BK-GCS-PEDCO-120-PR-PI-0022 | - | V-2205 |  | FUEL GAS K.O. DRUM |  | - |  | FUEL GAS | FUEL GAS | GAS | 33.6 | 85 | 4.9 | 18.2 | 1.46 | 0.69 | 11.24 | - | 0-100 | 2" | 300 | 500 | Yes
D02
D02
D02
D02
D02