## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0014_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1963 |  |  | Transmital Date: 25 Mar 2023
Document Title: Data Sheets For Corrosion Coupon/ Probe |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1963 |  |  | Transmital Date: 25 Mar 2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DT-0014_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | اظهارنظر در خصوص داده برگ ادوات پایش خوردگی پس از نهایی سازی مدرک مطالعات خوردگی و انتخاب مواد و همچنین نقشه های P&ID امکان پذیر می باشد.لیکن در این پروژه مدرک مطالعات خوردگی و انتخاب مواد نهایی نشده است. ضروریست پس از تکمیل مدارک ، مجددا می بایست برای بررسی ارسال گردد. |  | 1402/2294/65472 | 1402/02/24 | با توجه به صورت جلسه تاریخ 1402/03/24 اهواز، موارد خوردگی در این پروژه نهایی گردید که منجر به تغییری در متریال ، ضخامت و C. A. خطوط نشد و لذا خواهشمند است داده برگ برای تایید نهایی بررسی گردید.
2 | به منظور سهولت تعویض و اجتناب از ایجاد نقطه مرده در سامانه لوله کشی ، برای موقعیت CC-2162 (نصب بر روی مخزن) ACCESS FITTING از نوع FLARE WELD مورد تاکید می باشد. ضمنا همانگونه که در مکاتبات قبلی نیز تاکید گردید به منظور بررسی سهولت نصب رتریور فاصله و محل نصب (ارتفاع تا کف و فضای مانور عملیاتی ) در داده برگ مشخص گردد. |  | 1402/2294/65472 | 1402/02/24 | با توجه به نظر کارفرمای محترم ارتفاع نصب در داده برگ اضافه گردید. همچنین با توجه به مدارک spec. به منظور تسهیل در نصب و تعمیرات و همچنین سهولت مسدود کردن نازل ها در زمان تست مخزن، استفاده از flange برای نصب cc روی تانک توصیه میگردد.
3 | پیرو مکاتبات قبلی در خصوص موقعیت های CC/CP-2111 محل نصب به نقطه بعد از محل تزریق مواد شیمیایی با فاصله مناسب تغییر داده شود. |  | 1402/2294/65472 | 1402/02/24 | این مدرک بر اساس مدرک P&ID تهیه شده است و نقطه نظر کارفرمای محترم مبنی بر جابجایی محل نصب بر روی آن مدرک بیان گردد.
4
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: