## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0004_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1973 |  |  | Transmital Date: 25 Mar 2023
Document Title: Data Sheets For Pressure/Diff. Pressure Transmitter |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1973 |  |  | Transmital Date: 25 Mar 2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-DT-0004_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-02-07360 | 2023-04-08 | ملاحظه گردید.
2 | در صورت تغيير در هر يك از مدارك مرتبط مانند P&ID، اين مدرك نيز بروز رساني گردد. |  | BK-SUR-ENG-INS-02-07360 | 2023-04-08 | بروز رسانی گردید.
3 | اين مدرك با مدرك Instrument Index تناقض دارد براي مثال تگ PT-2301 در مدرك وجود ندارد. موارد اصلاح گردد. |  | BK-SUR-ENG-INS-02-07360 | 2023-04-08 | اصلاح گردید.
4 | باتوجه به تغييرات قطعي در برخي داده هاي فشاري تجهيزات، لطفا مدرك مذكور مطابق آخرين ويرايش تاييد شده P&ID اصلاح گردد.به عنوان نمونه آيتمهاي شماره هاي 13 و14 و 15PIT-2121A/B/C |  | BK-SUR-ENG-INS-02-07360 | 2023-04-08 | اصلاح گردید.
5 | Manifold rating براي تگ PIT-2104 كلاس 6000 در نظر گرفته شود. |  | BK-SUR-ENG-INS-02-07360 | 2023-04-08 | اصلاح گردید.
6 | در خصوص نوت 5: تمامي ترانسميترها Hart باشند.و اين مورد اصلاح گردد. |  | BK-SUR-ENG-INS-02-07360 | 2023-04-08 | اصلاح گردید.
7 | SIL مورد نياز بر اساس جلسات SILstudy در قالب يك ستون اضافه گردد. |  | BK-SUR-ENG-INS-02-07360 | 2023-04-08 | در ستون سیستم اضافه گردید.
8 | تعداد Electrical Connection ها مشخص گردد. |  | BK-SUR-ENG-INS-02-07360 | 2023-04-08 | اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date:8 Apr 2023 |  |  |  |  | Date: