## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0007_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1237 |  |  | Transmital Date: 16-Aug-2022
Document Title: Capacitor Banks Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-EL-TR-1237 |  |  | Transmital Date:16-َAug-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0007_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به وجود فیوز های استریکرپین در مدار و عملکرد کنتاکتور در صورت سوختن هر فیوز، از رله PHC به چه منظوری استفاده شده است؟ |  | 1401-2294-205602 | 1401-06-09 | رله PHC جهت حفاظت از نامتعادلی ولتاژ استفاده می گردد. در صورتیکه جابه جایی فاز (ولو عدم سوختن فیوز) به وجود آید، این رله تشخیص می دهد و بدین منظور از این رله استفاده شده است.
2 | محاسبات تعیین سطح اتصال کوتاه 31.5 KA برای باس تابلوی بانک خازنی ارائه شود. |  | 1401-2294-205602 | 1401-06-09 | سطح اتصال کوتاه تابلوی بانک خازنی بر اساس سطح اتصال کوتاه تابلوی بالادست LV خود 50 کیلوآمپر باید باشد که در داده برگه اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 12-Mar-22 |  |  |  |  | Date: