## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LD-0001_D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1720 |  |  | Transmital Date: 20-Dec-2022
Document Title: Control Logic Diagram For LV Incomers and bus tie |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0109-EL-TR-1720 |  |  | Transmital Date: 20-Dec-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-LD-0001_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحه 11 از 14، مربوط به حالت بستن دستی کوپلر 1، فانکشن Open Command PB می بایست به Close Command PB اصلاح گردد. |  | 1401-2294-422794 | 1401-11-05 | اعمال گردید.
2 | صفحه 12 از 14، مربوط به حالت بستن دستی کوپلر 2، فانکشن Open Command PB می بایست به Close Command PB اصلاح گردد. |  | 1401-2294-422794 | 1401-11-05 | اعمال گردید.
3 | صفحات 9 تا 13 عبارت Manual Operation در پایین صفحه متناسب با عملیات نمایش داده شده در آن صفحه تکمیل گردد. به عنوان نمونه عبارت manual Operation در صفحه 9 به عبارت manual Operation-Incoming A Closing اصلاح شود. |  | 1401-2294-422794 | 1401-11-05 | اعمال گردید.
4 | یک صفحه مجزا برای کلید محلی دیزل DGCB در مدرک اضافه و منطق مرتبط با باز و بسته شدن آن در مدرک نمایش داده شود. جهت بستن کلید محلی دیزل، لازم است که کلید باس کوپلر 2 باز باشد. |  | 1401-2294-422794 | 1401-11-05 | در صفحه آخر، لاجیک مربوط به کلید DGCB آورده شده است. طبق این لاجیک و هماهنگییهایی که در زمان خرید دیزل انجام می گردد، سازنده دیزل موظف است سیگنالهای مربوط به تابلوی LV را در مدار قطع و وصل کلید DGCB اعمال نماید. لذا از آوردن صفحه ای مجزا صرف نظر می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 02-Jan-23 |  |  |  |  | Date: