## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 10
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0001 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | SEP.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  | JUL.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | Client Approval
Class: 1 |  |  |  | Client Doc. Number: F9Z-708922
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for Client Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 10
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0001 |  | D02
REVISION RECORD SHEET
Page | D00 | D02 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D02 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 |  | X | X | [5 empty] | 73
10 |  | X | X | [5 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 10
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0001 | D02
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## NOTES
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 10
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0001 | D02
GENERAL NOTES:
1- Pressure elements shall be capable of withstanding intermittent over-ranging to 1.3 times the maximum scale reading.
2- Ranges shall be selected suitable to have the operating pressure in the middle third of the scale.
3- Vendor is responsible for applying suitable accessories to prevent damage and to reach required accuracy for PG.
4- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
5- Gauges shall be supplied with syphon on steam services which operating temperatures are more than 100⁰c.
6- Tag plate as per Specification for Instrumentation, shall be stainless steel 304 SS (VTC). Following details shall be engraved on them:
- Tag Number - Range limit - Service - Manufacturer model and serial number
7- Weep hole shall be provided on the case bottom of all gauges.
8- Material Test Certificate and Calibration Certificate for all gauges to be submitted by vendor.
9- Each pressure gauge which doesn’t have Diaphragm Seal, shall be supplied with a Two way (valve) manifold (block & bleed manifold) by vendor (Process Conn. 1/2"NPTF, 316 S.S.).
10- Environmental Condition For Field Instrumentation Of BINAK Complex Shall Be Considered As Per The Following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % (Note */ Note** DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
11. Will be finallized as per Safety Department information.

## PG
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 5 از 10
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO | 120 | IN | DT | 0001 | D02
PRESSURE GAUGE
| GENERAL | 1 | Tag No. |  |  | P&ID No. |  |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6
|  | 2 | Service |  |  | Piping Class |  |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6
|  | 3 | Area Clacification | [6 empty] | Zone 2, IIB T4
| PROCESS CONDITION | 4 | Fluid |  |  | Phase |  |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6
|  | 5 | Operating. Pressure |  |  | Design. Pressure |  |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6 |  | (barg)
|  | 6 | Operating. Temperature |  |  | Design. Temperature |  |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6 |  | (°C)
|  | 7 | Min. Design Metal Temperature | [6 empty] | SEE PAGE 6 | [7 empty] | (°C)
|  | 8 | Range | [6 empty] | SEE PAGE 6
| GAUGE | 9 | Type | [6 empty] | Pressure Gauge-Direct Reading
|  | 10 | Instrument Range | [6 empty] | SEE PAGE 6
|  | 11 | Liquid Filled | [6 empty] | Silicon Oil - SEE PAGE 6~9 |  |  |  | (Note 5)
|  | 12 | Mounting | [6 empty] | Direct
|  | 13 | Dial Size |  | Dial Color |  |  | Zero Adjustment |  | 150 mm |  |  | White with black lettering |  |  |  | Adjustable pointer
|  | 14 | Case Material |  |  |  | Ring Material |  |  | 304 SS (Note 2 & 9) |  |  |  | 304 SS
|  | 15 | Blow-Out Protection | [6 empty] | Required-Back
|  | 16 | Windows Material |  |  |  | Dial Material |  |  | Shatter proof glass |  |  |  | Aluminum
|  | 17 | Pressure Element Type | [6 empty] | SEE PAGE 6
|  | 18 | Pressure Element Material |  |  |  | Stem Material |  |  | SEE PAGE 6 |  |  |  | 316 SS
|  | 19 | Connection Material | [6 empty] | 316 S.S
|  | 20 | Connection Size | [6 empty] | 1/2 " NPT
|  | 21 | Connection Location | [6 empty] | Bottom
|  | 22 | Movement Material | [6 empty] | 316 S.S
|  | 23 | Nominal Accuracy | [6 empty] | 0.5% F.S
|  | 24 | Ingress Protection | [6 empty] | IP-65 as minimum
| DIAPHRAGM SEAL | 25 | Type | [6 empty] | N/A
|  | 26 | Size (In) | [6 empty] | N/A
|  | 27 | Diaphragm Material | [6 empty] | N/A
|  | 28 | Fill Fluid | [6 empty] | N/A
|  | 29 | Capillary Length | [6 empty] | N/A
|  | 30 | Capillary Material | [6 empty] | N/A
31
| OPTIONS | 32 | Movement Damping | [6 empty] | SEE PAGE 6
|  | 33 | Overrange Protection | [6 empty] | SEE PAGE 6 (1.3 of F.S) (Note 7)
|  | 34 | Siphon |  |  | Material |  |  |  | SEE PAGE 6 | [5 empty] | 316 S.S
|  | 35 | Manifold |  |  | Body Material |  |  |  | 2 Way Manifold | [5 empty] | 316 S.S
|  | 36 | Process Connection |  |  | Rating |  |  |  | SEE PAGE 6 (Note 6) | [5 empty] | SEE PAGE 6
|  | 37 | Manifold Model |  |  | Manifold Manufacturer |  |  |  | VTA | [5 empty] | VTA
|  | 38 | NACE Requirements | [6 empty] | SEE PAGE 6 |  |  |  | (Note 1)
39
40
| PURCHASING DATA | 41 | Model No. |  |  | Manufacturer |  |  |  | (Note 8) | [5 empty] | (Note 8)
|  | 42 | Supplier |  |  | Order |  |  |  | (Note 8) | [5 empty] | (Note 8)
43
44
| NOTES : | VTA : Vendor to Advise
(1) NACE-MR-0175/ISO 15156 requirements shall be covered where Piping/Pipeline Material Specification recommended.
(2) Window shall be heavy plate glass, breakage resistance and shatter proof.
(3) Pressure gauges shall be double scale type (Bar and Psi).
(4) All gauges shall be equipped with screw driver slot type adjustment for calibration purposes.
(5) Oil-filled system or Pulsation dampeners shall be supplied for all pressure instruments and gauges in vibrating or pulsating services.
(6) 1/2"NPT for Instrument/Process connection and 1/4" NPT for Drain Connection-All Manifolds, Pulsation Dampners and Siphons shall be suitable for connecting to gauges (1/2" NPT). And the material shall be 316 SS.
(7) Over range protection shall be 1.3 times the maximum range.
(8) Will be finalized later at the purchasing time.
(9) Cases for pressure gauges shall be solid front stainless steel.
(10) Weep hole shall be provided on the case bottom of all gauges.

## PG LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO |  | 120 | IN |  | DT |  | 0001 |  | D02
PRESSURE GAUGE
Rev. | Item No. | Tag No. | P&IDs No. | Service. | LINE/ EQUIPMENT | Piping Class | Manifold Rating | Process Connection | Fluid | Phase | Operating Pressure (barg) | Design Pressure (barg) | Operating Temperature (°C) | Design Temperature(°C) | Instrument Range (barg) | Liquid. Filled | Press. Element Type | Press. Element Material | Movement Dampener (Snubber) | Over Range Protection | Siphon | Diaphragm Seal | Nace | Model | Remark
D02-Modified | 1 | PG-2101 | BK-GCS-PEDCO-120-PR-PI-0002 | EXISTING GAS PIG RECEIVER | GAS-111-0001-AN07-6"-PT | AN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 7.5 | 18.2 | 46.11/26.67 | 85 | 0-16 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 2 | PG-2102 | BK-GCS-PEDCO-120-PR-PI-0002 | EXISTING GAS PIG RECEIVER | GAS-111-0001-AN07-6"-PT | AN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 7.5 | 18.2 | 46.11/26.67 | 85 | 0-16 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 3 | PG-2103 | BK-GCS-PEDCO-120-PR-PI-0003 | GAS PIG RECEIVER | GAS-111-0008-FN07-8"-PT | FN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 7.5 | 175 | 15.5-32 | 85 | 0-16 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 4 | PG-2104 | BK-GCS-PEDCO-120-PR-PI-0003 | GAS PIG RECEIVER | GAS-111-0008-FN07-8"-PT | FN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 7.5 | 175 | 15.5-32 | 85 | 0-16 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 5 | PG-2111 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | SLUG CATCHER DRUM | V-2104 | AN07 | #6000 | 1/2" NPT | HYDROCARBON/WATER | GAS | 5.5 | FV/9 | 15.5-32 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 6 | PG-2114A | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | SLUG PUMPS | CDH-111-0010-AS00-4"-NP | AS00 | #3000 | 1/2" NPT | WATER | LIQUID | 5.5 | 13.9 | 23.22/8.82 | 85 | 0-1 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02-Modified | 7 | PG-2113A | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | SLUG PUMPS | CDH-111-0012-CN05-3"-PT | CN05 | #6000 | 1/2" NPT | WATER | LIQUID | 19.5 | 47.7 | AMB | 85 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 8 | PG-2113B | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | SLUG PUMPS | CDH-111-0013-CN05-4"-PT | CN05 | #6000 | 1/2" NPT | WATER | LIQUID | 19.5 | 47.7 | AMB | 85 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 9 | PG-2114B | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | SLUG PUMPS | CDH-111-0011-AS00-4"-PT | AS00 | #3000 | 1/2" NPT | WATER | LIQUID | 5.5 | 13.9 | 23.22/8.82 | 85 | 0-1 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02-Modified | 10 | PG-2114 | BK-GCS-PEDCO-120-PR-PI-0005 | INLET KNOCK OUT DRUM | V-2105 | AN07 | #6000 | 1/2" NPT | HYDROCARBON/WATER | GAS | 5.3 | FV/9 | 19-37 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 11 | PG-2115 | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | GAS-111-0025-AN07-10"-PT | AN07 | #6000 | 1/2" NPT | HYDROCARBON/WATER | GAS | 5.1 | 18.2 | 19-37 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 12 | PG-2121A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #A | V-2101-A | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 5.1 | FV/22 | 19-37 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 13 | PG-2121B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #B | V-2101-B | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 5.1 | FV/22 | 19-37 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 14 | PG-2121C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #C | V-2101-C | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 5.1 | FV/22 | 19-37 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 15 | PG-2122A | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | 1ST STAGE GAS COMPRESSOR TRAIN#A | GAS-111-0031A-CN05-8"-ET | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 4.9 | 47.7 | 18-35 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 16 | PG-2123A | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | 1ST STAGE GAS COMPRESSOR TRAIN#A | GAS-111-0036A-CN05-6"-NP | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 19 | 47.7 | 113/124 | 155 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 17 | PG-2122B | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | 1ST STAGE GAS COMPRESSOR TRAIN#B | GAS-111-0031B-CN05-8"-ET | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 4.9 | 47.7 | 18-35 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 18 | PG-2123B | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | 1ST STAGE GAS COMPRESSOR TRAIN#B | GAS-111-0036B-CN05-6"-NP | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 19 | 47.7 | 113/124 | 155 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 19 | PG-2122C | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | 1ST STAGE GAS COMPRESSOR TRAIN#C | GAS-111-0031C-CN05-8"-ET | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 4.9 | 47.7 | 18-35 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 20 | PG-2123C | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | 1ST STAGE GAS COMPRESSOR TRAIN#C | GAS-111-0036C-CN05-6"-NP | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 19 | 47.7 | 113/124 | 155 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 21 | PG-2124A | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) | 1ST STAGE GAS COMPRESSION AIR COOLER TRAIN #A | GAS-111-0037A-CS00-6"-NP | CS00 | #3000 | 1/2" NPT | HYDROCARBON | GAS/LIQUID | 18.3 | 30.3 | 60 | 155 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 22 | PG-2124B | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) | 1ST STAGE GAS COMPRESSION AIR COOLER TRAIN #B | GAS-111-0037B-CS00-6"-NP | CS00 | #3000 | 1/2" NPT | HYDROCARBON | GAS/LIQUID | 18.3 | 30.3 | 60 | 155 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 23 | PG-2124C | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) | 1ST STAGE GAS COMPRESSION AIR COOLER TRAIN #C | GAS-111-0037C-CS00-6"-NP | CS00 | #3000 | 1/2" NPT | HYDROCARBON | GAS/LIQUID | 18.3 | 30.3 | 60 | 155 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 24 | PG-2131A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | 2ND STAGE GAS COMPRESSOR CUCTION DRUM TRAIN #A | V-2102-A | CS00 | #3000 | 1/2" NPT | HYDROCARBON | GAS | 18.3 | FV/22 | 60 | 115.4 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 25 | PG-2131B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | 2ND STAGE GAS COMPRESSOR CUCTION DRUM TRAIN #B | V-2102-B | CS00 | #3000 | 1/2" NPT | HYDROCARBON | GAS | 18.3 | FV/22 | 60 | 115.4 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 26 | PG-2131C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | 2ND STAGE GAS COMPRESSOR CUCTION DRUM TRAIN #C | V-2102-C | CS00 | #3000 | 1/2" NPT | HYDROCARBON | GAS | 18.3 | FV/22 | 60 | 115.4 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 27 | PG-2132A | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | 2ND STAGE GAS COMPRESSOR TRAIN#A | GAS-111-0044A-CN05-6"-ET | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 18.1 | 47.7 | 59-60 | 115.4 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 28 | PG-2133A | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | 2ND STAGE GAS COMPRESSOR TRAIN#A | GAS-111-0051A-FN05-6"-IS | FN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 54.8 | 90 | 142-150 | 175 | 0-100 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 29 | PG-2132B | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | 2ND STAGE GAS COMPRESSOR TRAIN#B | GAS-111-0044B-CN05-6"-ET | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 18.1 | 47.7 | 59-60 | 115.4 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 30 | PG-2133B | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | 2ND STAGE GAS COMPRESSOR TRAIN#B | GAS-111-0051B-FN05-6"-IS | FN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 54.8 | 90 | 142-150 | 175 | 0-100 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 31 | PG-2132C | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | 2ND STAGE GAS COMPRESSOR TRAIN#C | GAS-111-0044C-CN05-6"-ET | CN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 18.1 | 47.7 | 59-60 | 115.4 | 0-40 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 32 | PG-2133C | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | 2ND STAGE GAS COMPRESSOR TRAIN#C | GAS-111-0051C-FN05-6"-IS | FN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 54.8 | 90 | 142-150 | 175 | 0-100 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 33 | PG-2134A | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN#A | GAS-111-0058A-FS00-6"-NP | FS00 | #6000 | 1/2" NPT | HYDROCARBON | GAS/LIQUID | 54.1 | 62.4 | 60 | 175 | 0-100 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 34 | PG-2134B | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN#B | GAS-111-0058B-FS00-6"-NP | FS00 | #6000 | 1/2" NPT | HYDROCARBON | GAS/LIQUID | 54.1 | 62.4 | 60 | 175 | 0-100 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 35 | PG-2134C | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN#C | GAS-111-0058C-FS00-6"-NP | FS00 | #6000 | 1/2" NPT | HYDROCARBON | GAS/LIQUID | 54.1 | 62.4 | 60 | 175 | 0-100 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 36 | PG-2142 | BK-GCS-PEDCO-120-PR-PI-0012 | GAS COMPRESSION DISCHARGE DRUM | V-2103 | FN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 53.9 | 90 | 59-60 | 130 | 0-100 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 37 | PG-2141 | BK-GCS-PEDCO-120-PR-PI-0012 | GAS COMPRESSION DISCHARGE DRUM | V-2103 | FN05 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 53.9 | FV/62 | 59-60 | 130 | 0-100 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 38 | PG-2162 | BK-GCS-PEDCO-120-PR-PI-0014 | GLYCOL TRANSFER PUMP | TEG-111-0004-AN04-2"-PT | AN04 | #3000 | 1/2" NPT | LEAN GLYCOL | LIQUID | 0.02 | 18.2 | AMB | 85 | 0-0.25 | Yes | Diaphragm | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 39 | PG-2163A | BK-GCS-PEDCO-120-PR-PI-0014 | GLYCOL TRANSFER PUMP | TEG-111-0002-AN04-2"-PT | AN04 | #3000 | 1/2" NPT | LEAN GLYCOL | LIQUID | 2.1 | 18.2 | AMB | 85 | 0-4 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 40 | PG-2163B | BK-GCS-PEDCO-120-PR-PI-0014 | GLYCOL TRANSFER PUMP | TEG-111-0006-AN04-2"-PT | AN04 | #3000 | 1/2" NPT | LEAN GLYCOL | LIQUID | 2.1 | 18.2 | AMB | 85 | 0-4 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 41 | PG-2161 | BK-GCS-PEDCO-120-PR-PI-0014 | LEAN GLYCOL STORAGE TANK | TOP OF THE TK-2102 | AN07 | #6000 | 1/2" NPT | LEAN GLYCOL | GAS | 0.1 | FULL OF LIQUID + 160MBARG/-7MBARG | AMB | 85 | 0-0.25 | Yes | Diaphragm | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 42 | PG-2201 | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | Instrument Air Receiver | ISA-112-0012-AZ00-2"-NP | AZ00 | #3000 | 1/2" NPT | Air | GAS | 8 | 18.2 | 65 | 85 | 0-16 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 43 | PG-2202 | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | Instrument Air Receiver | V-2203 | AZ00 | #3000 | 1/2" NPT | Air | GAS | 8 | 12.5 | 65 | 85 | 0-16 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 44 | PG-2211 | BK-GCS-PEDCO-120-PR-PI-0016 | Nitrogen Reveiver | NIT-112-0021-AN01-2"-PT | AN01 | #3000 | 1/2" NPT | Nitrogen | GAS | 8 | 18.2 | 60 | 85 | 0-16 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 45 | PG-2212 | BK-GCS-PEDCO-120-PR-PI-0016 | Nitrogen Reveiver | V-2204 | AN01 | #3000 | 1/2" NPT | Nitrogen | GAS | 8 | 12.5 | 60 | 85 | 0-16 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 46 | PG-2221 | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | closed drain drum | V-2202 | AN07 | #6000 | 1/2" NPT | HYDROCARBON/WATER | LIQUID | 0.5 | FV/6.0 | AMB | 85 | 0-1 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02-Modified | 47 | PG-2251 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) | LP flare K.O.drum | V-2201 | AN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 0.5 | FV/6.0 | 32 | 85 | 0-1 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02-Modified | 48 | PG-2251A | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) | LP flare K.O.drum pump | CDH-112-0038-AN07-2"-PT | AN07 | #6000 | 1/2" NPT | HYDROCARBON | LIQUID | 1.6 | 18.2 | AMB | 85 | 0-4 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02-Modified | 49 | PG-2251B | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) | LP flare K.O.drum pump | CDH-112-0037-AN07-2"-PT | AN07 | #6000 | 1/2" NPT | HYDROCARBON | LIQUID | 1.6 | 18.2 | AMB | 85 | 0-4 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02-Modified | 50 | PG-2272 | BK-GCS-PEDCO-120-PR-PI-0022 | FUEL GAS | FLG-111-0004-AN07-2"-PT | AN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 5.1 | 18.2 | 19-37 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 51 | PG-2273 | BK-GCS-PEDCO-120-PR-PI-0022 | FUEL GAS | V-2205 | AN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 4.9 | FV/9 | 19-37 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 52 | PG-2271 | BK-GCS-PEDCO-120-PR-PI-0022 | FUEL GAS | FLG-112-0010-AN07-2"-PT | AN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 4.9 | 18.2 | 33.6 | 85 | 0-10 | Yes | Bourdon | SS 316L | No | No | No | No | Yes | VTA | Note 1
D02-Modified | 53 | PG-2274 | BK-GCS-PEDCO-120-PR-PI-0022 | FUEL GAS | FL-112-0040-AN07-2"-PT | AN07 | #6000 | 1/2" NPT | HYDROCARBON | GAS | 0.5 | 18.2 | 33.6 | 85 | 0-1 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02-Modified | 54 | PG-2282 | BK-GCS-PEDCO-120-PR-PI-0023 | OIL | V-2206 | AN01 | #3000 | 1/2" NPT | HYDROCARBON | LIQUID/OIL | 0.95 | 18.2 | 5-50 | 85 | 0-2 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 56 | PG-2283 | BK-GCS-PEDCO-120-PR-PI-0023 | OIL | V-2206 | AN01 | #3000 | 1/2" NPT | HYDROCARBON | LIQUID/OIL | 0.95 | 18.2 | 5-50 | 85 | 0-2 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 58 | PG-2291 | BK-GCS-PEDCO-120-PR-PI-0024 | Potable Water | PTW-112-0003-AZ00-2"-NP | AZ00 | #3000 | 1/2" NPT | Water | Liquid | 1.95 | 18.2 | AMB | 85 | 0-4 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 59 | PG-2292 | BK-GCS-PEDCO-120-PR-PI-0024 | Potable Water | PTW-112-0001-AZ00-2"-NP | AZ00 | #3000 | 1/2" NPT | Water | Liquid | 0.15 | 18.2 | AMB | 85 | 0-0.25 | Yes | Diaphragm | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 60 | PG-2293 | BK-GCS-PEDCO-120-PR-PI-0025 | RICH GLYCOL | V-2107 | AN04 | #3000 | 1/2" NPT | RICH GLYCOL | Liquid | 2.1 | 18.2 | AMB | 85 | 0-4 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 61 | PG-2294 | BK-GCS-PEDCO-120-PR-PI-0025 | Right Glycol | TEG-111-001-AN04-2"-PT | AN04 | #3000 | 1/2" NPT | RICH GLYCOL | Liquid | 0.01 | FV/3.5 | AMB | 85 | 0-4 | Yes | Bourdon | SS 316L | No | No | No | No | No | VTA | Note 1
D02-Modified | 62 | PG-2295 | BK-GCS-PEDCO-120-PR-PI-0025 | GLYCOL SUMP DRUM | NIT-111-0009-AN04-1"-PT | AN04 | #3000 | 1/2" NPT | NITROGEN | GAS | 0.5 | 18.2 | AMB | 85 | 0-1 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02-Modified | 63 | PG-2301 | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 8) | Fire Water | FWA-113-0001-AN04-3"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 11.3 | 17 | AMB | 85 | 0-20 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 64 | PG-2305 | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-0025-AN04-12"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 11.3 | 17 | AMB | 85 | 0-20 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 65 | PG-2303A | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-0027-AN04-2"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 1 | 1.5 | AMB | 85 | 0-2 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 66 | PG-2304A | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-0029-AN04-2"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 11.3 | 17 | AMB | 85 | 0-20 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 67 | PG-2303B | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-0026-AN04-2"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 1 | 1.5 | AMB | 85 | 0-2 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 68 | PG-2304B | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-0028-AN04-2"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 11.3 | 17 | AMB | 85 | 0-20 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 69 | PG-2301A | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-0006-AN04-12"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 1 | 1.5 | AMB | 85 | 0-2 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 70 | PG-2302A | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-00022-AN04-10"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 11.3 | 17 | AMB | 85 | 0-20 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 71 | PG-2301B | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-0006-AN04-12"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 1 | 1.5 | AMB | 85 | 0-2 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02-Modified | 72 | PG-2302B | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 8) | Fire Water | FWA-113-0021-AN04-10"-PT | AN04 | #3000 | 1/2" NPT | Water | Liquid | 11.3 | 17 | AMB | 85 | 0-20 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | VTA | Note 1
D02
D02
D02
D02
D02
D02
D02
D02

## PDG
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE
شماره پیمان: | [6 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 10
9184 – 073 - 053 | [6 empty] | BK | GCS | PEDCO | 120 | IN |  | DT | 0001 | D02
Differential Pressure Gauge
GENERAL |  | 1 | Item | [8 empty] | See Page 10
|  | 2 | Tag Number | [8 empty] | See Page 10
|  | 3 | Service | [8 empty] | See Page 10
|  | 4 | Line No. | [8 empty] | See Page 10
|  | 5 | Equipment No. |  |  |  | P&ID No. |  |  |  |  | See Page 10 |  |  |  | See Page 10
|  | 6 | Area Classification | [8 empty] | Zone 2, IIB T4
PROCESS CONDITIONS |  | 7 | Fluid |  |  |  | Fluid State |  |  |  |  | See Page 10 |  |  |  | See Page 10
|  | 8 | Max Press. Oper. |  |  |  | Design Pressure |  |  |  |  | See Page 10 |  |  | barg | See Page 10 | barg
|  | 9 | Oper. Temp. |  |  |  | Design Temperature |  |  |  |  | See Page 10 |  |  |  | See Page 10 | °C | ؛C
MANIFOLD |  | 10 | Manifold Type |  |  | Manifold Material | [5 empty] | 5 Way Manifold |  |  |  | 316 S.S.
|  | 11 | Connection |  |  | Manifold Rating | [5 empty] | 1/2" NPTF (Note 6) |  |  |  | (Note 11)
CASE |  | 12 | Case Type |  |  | Case Style | [5 empty] | Silicon Oil Filled |  |  |  | weather proof (IP 65)
|  | 13 | Case Material |  |  | Case Size | [5 empty] | 304 S.S. |  |  |  | 150 mm
|  | 14 | Case Pressure Relief | [8 empty] | Yes
|  | 15 | Conn. Location |  |  | Proc. Connection | [5 empty] | bottom |  |  |  | See Page 10
|  | 16 | Ring Style |  |  | Ring Material | [5 empty] | VTA |  |  |  | 304 S.S.
|  | 17 | Mounting Type |  |  | Blow-out protection | [5 empty] | Direct |  |  |  | Back
|  | 18 | Socket Material | [8 empty] | 316 S.S.
|  | 19 | Window Material | [8 empty] | Shatterproof glass
|  | 20 | Seal / O-Ring Material | [8 empty] | VTA
ELEMENT |  | 21 | Liquid Fill Material | [8 empty] | VTA
|  | 22 | Element Type |  |  | Element Material | [5 empty] | Diaphragm |  |  |  | 316 S.S.
|  | 23 | Movement Style |  |  | Movement Material | [5 empty] | VTA |  |  |  | 316 S.S.
|  | 24 | Over Range Protection | [8 empty] | 1.3 times of maximum operating pressure
|  | 25 | Accuracy | [8 empty] | ±0.5% of F.S.
|  | 26 | Internal Stop | [8 empty] | Yes
|  | 27 | Measuring Range | [8 empty] | See Page 10 |  |  |  | barg
DIAL |  | 28 | Dial Scale Type |  |  | Dial Material | [5 empty] | Dual indicating scales (barg/psig) |  |  |  | aluminum
|  | 29 | Dial Color | [8 empty] | black marks on white background
|  | 30 | Zero Adjustment | [8 empty] | Adjustable pointer
ACCESSORY |  | 31 | Syphon |  |  | Material | [5 empty] | See Page 10 |  |  |  | 316 S.S.(if necessary)
|  | 32 | Pulsation Damper |  |  | Material | [5 empty] | See Page 10 |  |  |  | 316 S.S.(if necessary)
|  | 33 | Over Range Protection |  |  | Material | [5 empty] | See Page 10 |  |  |  | 316 S.S.(if necessary)
|  | 34 | End Connection | [8 empty] | 1/2" NPT (Note 6)
DIAPHRAGM SEAL |  | 35 | Seal Type | [8 empty] | N/A
|  | 36 | Instrument Conn. |  |  | Process Conn. | [5 empty] | N/A |  |  |  | N/A
|  | 37 | Diaphragm Extension Length | [8 empty] | N/A
|  | 38 | Diaphragm Material | [8 empty] | N/A
|  | 39 | Capillary Material |  |  | Capillary Length | [5 empty] | N/A |  |  |  | N/A
|  | 40 | Housing Mtrl. |  | Upper | Lower | [5 empty] | N/A |  |  |  | N/A
|  | 41 | Bolting Material | [8 empty] | N/A
|  | 42 | Gasket / O-Ring Material | [8 empty] | N/A
|  | 43 | Fill Fluid Material | [8 empty] | N/A
SPECIAL |  | 44 | NACE MR0175/ISO 15156 Compliance | [8 empty] | See Page 10
PURCHASE |  | 45 | Manufacturer | [8 empty] | (Note 8)
|  | 46 | Model | [8 empty] | (Note 8)
NOTES: |  |  |  | VTA : Vendor to Advise
N/A: Not Applicable
(1) NACE-MR-0175/ISO 15156 requirements shall be covered where Piping/Pipeline Material Specification recommended.
(2) Window shall be heavy plate glass, breakage resistance and shatter proof.
(3) Pressure gauges shall be double scale type (Bar and Psi).
(4) All gauges shall be equipped with screw driver slot type adjustment for calibration purposes.
(5) Oil-filled system or Pulsation dampeners shall be supplied for all pressure instruments and gauges in vibrating or pulsating services.
(6) 1/2"NPT for Instrument/Process connection and 1/4" NPT for Drain Connection-All Manifolds, Pulsation Dampners and Siphons shall be suitable for connecting to gauges (1/2" NPT). And the material shall be 316 SS.
(7) Over range protection shall be 1.3 times the maximum range.
(8) Will be finalized later at the purchasing time.
(9) Cases for pressure gauges shall be solid front stainless steel.
(10) Weep hole shall be provided on the case bottom of all gauges.
(11) For manifoled rating, Bolt & Gasket material refer to "Piping Material Specification Doc No.: BK-GCS-PEDCO-120-PI-SP-0001"
(12) Gauge pointer shall be adjustable (micro meter adjustment) without removal from pinion shaft.
D02

## PDG LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO |  | 120 | IN |  | DT |  | 0001 |  | D02
DIFFERENTIAL PRESSURE GAUGE
Rev. | Item No. | Tag No. | P&IDs No. | Service. | LINE/ EQUIPMENT | Piping Class | Connection Rating | Process Connection | Fluid | Phase | Operating Pressure (barg) | Design Pressure (barg) | Operating Temperature (°C) | Design Temperature(°C) | Instrument Range (mbarg) | Liquid. Filled | Press. Element Type | Press. Element Material | Movement Dampener (Snubber) | Over Range Protection | Siphon | Diaphragm Seal | Nace | Model | Remark
| 1 | PDG-2114A | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | BEFORE SLUG PUMP A | CDH-112-0010-AS00-4"-PT | AS00 | - | 1/2" NPT | WATER | LIQUID | 5.5 | 13.9 | 23.22/8.82 | 85 | 0-500 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
| 2 | PDG-2114B | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | BEFORE SLUG PUMP B | CDH-112-0011-AS00-4"-PT | AS00 | - | 1/2" NPT | WATER | LIQUID | 5.5 | 13.9 | 23.22/8.82 | 85 | 0-500 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
| 3 | PDG-2271 | BK-GCS-PEDCO-120-PR-PI-0022 | FUEL GAS K.O. DRUM | V-2205 | - | - | 1/2" NPT | HYDROCARBON | GAS | 4.9 | FV/9 | 33.6 | 85 | 0-500 | Yes | Bourdon | SS 316L | No | Yes | No | No | Yes | VTA | Note 1
D02
D02
D02