## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR LEVEL SWITCH
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0008 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEET FOR LEVEL SWITCH نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  |  | SEP.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  |  | SEP.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: F9Z-708929
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR LEVEL SWITCH
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0008 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR LEVEL SWITCH
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0008 | D02
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001-D04
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001-D04
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001-D02
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002-D00
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002-D01
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001-D04
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002-D06
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003-D06
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004-D06
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005-D06
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006-D06
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007-D06
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008-D06
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009-D06
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010-D06
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011-D06
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012-D06
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013-D06
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014-D06
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015-D06
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016-D06
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017-D06
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018-D07
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019-D06
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020-D06
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021-D05
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022-D06
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023-D06
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024-D06
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025-D06
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001-D04
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002-D02
|  | IPS Construction and Installation Standard for Level instruments | [6 empty] | IPS-C-IN-140
|  | IPS Engineering and Design Standard for Level instruments | [6 empty] | IPS-E-IN-140
|  | IPS Material and Equipment Standard for Level instruments | [6 empty] | IPS-M-IN-140
D02

## NOTES
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR LEVEL SWITCH
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0008 | D02
GENERAL NOTES:
1 - Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
2 - For level switches suitable sunshades shall be supplied by vendor.
3 - Vendor design shall be in accordance with : "Specification For Instrumentation, Doc. No. BK-GNRAL-PEDCO-000-IN-SP-0001" and all related spec.s for level switches.
4 -Vendor shall specify dead band of switches at quotation stage for client approval.
5 - Calibration scale shall be provided in switch to indicate exact set-point setting of switch.
6 - Vendor shall provide calibration certificate, factory visual and dimensional inspection report, hydrostatic pressure test certification, and mechanical test report.
7 - Level switches shall be fabricated according to IPS-M-IN-140.
8 - Level switches shall be provided with a stainless steel 304 SS (VTC) nameplate permanently fastened to the instrument. Following details shall be engraved on them:
• Tag Number • Manufacturer model and serial number • Service • Contact rating • Electrical classification and certification agency name and code • Project Information
9 - Environmental condition for field instrumentation of Binak oilfield shall be considered as per the following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: -5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
10- Internal stilling well should be supplied by the Vendor, and should have an inside diameter of at least 25mm larger than the displacer or float diameter. The stilling well shall be open at the bottom end, and should have a vent hole located above the maximum level.

## LS
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR LEVEL SWITCH
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT |  | 0008 |  | D02
LEVEL SWITCH
| GENERAL DATA |  | 1 | Tag No. | [8 empty] | SEE PAGE 6
|  |  | 2 | P & ID No. | [8 empty] | SEE PAGE 6
|  |  | 3 | Service | [8 empty] | SEE PAGE 6
|  |  | 4 | Equipment No. | [8 empty] | SEE PAGE 6
|  |  | 5 | Area Clacification | [8 empty] | ZONE 2, IIB T4
6
| OPERATING CONDITIONS |  | 7 | Upper Fluid |  |  | Lower Fluid | [5 empty] | SEE PAGE 6 |  |  |  | SEE PAGE 6
|  |  | 8 | Upper Phase |  |  | Lower Phase | [5 empty] | SEE PAGE 6 |  |  |  | SEE PAGE 6
|  |  | 9 | Operating Pressure |  |  | Design Pressure |  |  |  | (barg) |  | SEE PAGE 6 |  |  |  | SEE PAGE 6
|  |  | 10 | Operating Temperature |  |  | Design Temperature |  |  |  | (°C) |  | SEE PAGE 6 |  |  |  | SEE PAGE 6
|  |  | 11 | Upper Density |  |  | Lower Density |  |  |  | (kg/m3) |  | SEE PAGE 6 |  |  |  | SEE PAGE 6
12
13
| BODY/GAGE |  | 14 | Body/Cage Material | [8 empty] | SEE PAGE 6
|  |  | 15 | Head Orientation | [8 empty] | Top
|  |  | 16 | Connection Size & Rating | [8 empty] | SEE PAGE 6
|  |  | 17 | Flange Material | [8 empty] | SEE PAGE 6
|  |  | 18 | Length of Center To Center (C-C) |  |  |  | Set Point (mm) |  |  |  |  | N.A |  |  | SEE PAGE 6 (Note 1)
|  |  | 19 | Mounting | [8 empty] | Internal
20
| DISPLACER / FLOAT |  | 21 | Type | [8 empty] | SEE PAGE 6
|  |  | 22 | Insertion Depth | [8 empty] | VTA
|  |  | 23 | Displacer or Float Material | [8 empty] | 316 S.S
|  |  | 24 | Setting | [8 empty] | Adjustable / Internal
|  |  | 25 | Differential Gap (Fixed/Adj) | [8 empty] | Fixed
| SWITCH |  | 26 | Type | [8 empty] | Snap Acting with Hermetically Sealed (write protected)
|  |  | 27 | Quantity | [8 empty] | 2 x DPDT
|  |  | 28 | Setpoint | [8 empty] | SEE PAGE 6
|  |  | 29 | Ingress Protection | [8 empty] | IP-65 as minimum
|  |  | 30 | Electrical Certificate | [8 empty] | EExd IIB,T4
|  |  | 31 | Electrical Connection | [8 empty] | ISO M20 x 1.5
|  |  | 32 | Contact Rating | [8 empty] | 10A @ 110 VAC
|  |  | 33 | Load Type | [8 empty] | Inductive
|  |  | 34 | Case Material | [8 empty] | VTA
|  |  | 35 | Contacts (Open / Close) | [8 empty] | Normally Close
|  |  | 36 | On Level (Incr. / Decr.) | [8 empty] | SEE PAGE 6
|  |  | 37 | ACCURACY | [8 empty] | 1% OF SPAN
| OPTIONS |  | 38 | Tag Name Plate | [8 empty] | Required
|  |  | 39 | Cable Gland | [8 empty] | Required
|  |  | 40 | Vent/Drain Valve | [8 empty] | N.A
|  |  | 41 | NACE Requirement (As per MR0175/ISO 15156 Compliance) | [8 empty] | SEE PAGE 6
| PURCHASING DATA |  | 42 | Model |  |  | Manufacture | [5 empty] | Will be finalized later |  |  |  | Will be finalized later
|  |  | 43 | Supplier |  |  | Order | [5 empty] | Will be finalized later |  |  |  | Will be finalized later
44
| NOTES : | VTA : VENDOR TO ADVISE
(1) The location for installation will be finalized by process and mechanical departments.
(2) Safety area classification shall be hold until to be finalized in Doc.: Hazardous Area Classification Layout BK-GCS-PEDCO-120-SA-PY-0002.
-3

## LS LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR LEVEL SWITCH
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO |  | 120 | IN |  | DT | 0008 | D02
LEVEL SWITCH LIST
Rev. | Item No. | Tag No. | P&ID No. | Equipment No. | Height of the Equipment (m) | Fluide | Phase |  | Design Pressure (barg) | Operating Pressure (barg) | Design Temp. (°C) | Operating Temp. (°C) | Density (kg/m3) | Body/Cage MTR. | Size & Rating | Flange Material | C-C (mm) | Type | Set Point (mm) | On Level (Incr./Decr.) | Nace | Model | Remark
| 1 | LSLL-2301 | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 10) | TK-2301-A | 11 | FIRE WATER | L |  | 1.5 | 1 | 85 | AMB. | 1024 | 316 S.S | Side 2", Flanged, 300# RF | A-105 | N.A | Float-Type (Internal) | 850 | Decrease | NO | VTA
| 2 | LSLL-2302 | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 10) | TK-2301-B | 11 | FIRE WATER | L |  | 1.5 | 1 | 85 | AMB. | 1024 | 316 S.S | Side 2", Flanged, 300# RF | A-105 | N.A | Float-Type (Internal) | 850 | Decrease | NO | VTA
NOTE: |  | (1) G: GAS |  | L: LIQUID |  |  |  |  | NA: NOT APPLICABLE
D02
D02
D02