## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DG-0008_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1606 |  |  | Transmital Date: 26 Nov 2022
Document Title: Instrument & F&G Junction Box Termination Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1606 |  |  | Transmital Date: 26 Nov 2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DG-0008_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به تنوع و افزایش سیگنالها ، فهرست عناوین همراه با صفحه بندی جهت مدرک در نظر گرفته شود |  | 1401/2294/367610 | 1401/09/29 | اصلاح گردید
2 | صفحه 34 چک یک سیگنال ESD بعنوان SPARE در JB مربوط به DCS قرار دارد؟ |  | 1401/2294/367610 | 1401/09/29 | اصلاح گردید
3 | ارتباط سیگنالهای پنل های کنترل (DCS , ESD , UCP , LCP و LCP … ) با MCC از طریق IRP صورت گیرد |  | 1401/2294/367610 | 1401/09/29 | ارتباط سیگنالهای پنل های کنترل (DCS , ESD , UCP , LCP و LCP … ) با MCC از طریق IRP صورت می گیرد. این موضوع در طراحی رعایت شده است
4 | پنل کنترلی ( گرمکن ( BMS) بسته نمزدا با توجه به الزام استانداردی بایستی بصورت مستقل از DCS درنظر گرفته شود و ارتباطات لازم با توجه به مدارک سازنده پیش بینی گردد |  | 1401/2294/367610 | 1401/09/29 | در صورت وجود بسته نمزدا در این پروژه سیگنالهای آن بصورت جدا از DCS کابل کشی خواهند شد
5 | پس از تغییرات در مدارک پایه و مدارک سازندگان پکیج ها لازم است بروز رسانی صورت گیرد |  | 1401/2294/367610 | 1401/09/29 | با آخرین مدارک رفرنس مدرک بروز رسانی گردید. لازم بذکر پس از نهای شدن وندور پکیچ ها مدرک نهای سازی می گردد
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: