## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0005_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1159 |  |  | Transmital Date: 13-Jul-2022
Document Title: Area Electrical Cable Route & Section Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0104-EL-TR-1159 |  |  | Transmital Date: 13-Jul-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-PY-0005_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | عرض ترانشه در بعضی از مقاطع زیاد می باشد، مطابق نقشه IPS-D-EL-210 می توان، جهت کاهش عرض ترانشه ها کابل های قدرت و کنترل را بصورت 2 لایه در ترانشه قرار داد. |  | 1401-2294-172867 | 1401-05-20 | با توجه به عدم نهایی شدن لیست کابل ها، عرض ترانشه بزرگ تر در نظر گرفته شده است و در صورت نهایی شدن لیست کابل ها ترانشه متناسب و به روز رسانی می گردد.
2 | عمق ترانشه به 100 سانتیمتر افزایش یابد. |  | 1401-2294-172867 | 1401-05-20 | در ویرایش بعدی عمق ترانشه ها یک متر لحاظ خواهد شد.
3 | براساس شرح کار و مدارک پروژه ترانشه ها در محوطه پروژه بصورت بتنی می باشند، ترانشه خاکی فقط در محوطه خارج از فنس پروژه مجاز می باشد. |  | 1401-2294-172867 | 1401-05-20 | مطابق با شرح کار ترانشه در محوطه بتنی بصورت بتنی در نظر گرفته شده که با خاک پر می شود.
4 | در بخش Reference Drawing، شماره نقشه استاندارد IPS قید گردد. |  | 1401-2294-172867 | 1401-05-20 | استاندارد های IPS-D-EL-209 و IPS-D-EL-210 اضافه گردید.
5 | Tag کابل ها می بایست براساس موارد مندرج در نامه شماره 114025 مورخ 1401/04/03 و مطابق مدرک کابل لیست نمونه ارسالی اصلاح شوند. |  | 1401-2294-172867 | 1401-05-20 | تگ کابل ها مطابق با پیوست ارسالی کارفرمای محترم در ویرایش بعدی و در قسمت سکشن ها لحاظ می گردد.
6 | کاندویت (داکت) بانک می بایست بصورت مسلح اجرا گردد، لذا ضروری است، در این مدرک و یا در مدارک مرتبط جزئیات اجرایی آن نمایش داده شود. |  | 1401-2294-172867 | 1401-05-20 | در رفرنس مدارک به مدرک STANDARD DRAWING FOR ELECTRICAL CABLE TRENCH اشاره شده است در نتیجه داکت بانک ها به صورت مدرک فوق خواهد بود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 27-Jul-22 |  |  |  |  | Date: