## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0008_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1845 |  |  | Transmital Date: 06-FEB-2023
Document Title: Calculation Note For Cathodic Protection System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0111-EL-TR-1845 |  |  | Transmital Date: 06-FEB-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0008_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Page 9, Section 5.6, Structure data: Reference document for table.2 shall be mentioned. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | Confirmed |  |  | Noted and Closed.
2 | Page 9, Section 6, Calculation for pipeline: Required number of anodes based on anode weight shall be added. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | MMO anodes are stable anodes and don’t loose weight with time, so this comment is not applicable for MMO anodes |  |  | Noted and Closed.
3 | Page 9, Section 6.1, Surface calculation: There is conflict between this section and section 5.6, from point of view thickness of pipeline. It shall be clarify. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
4 | Page 10, Section 6.2, Current calculation: The reference of Maximum Operating Temperature in table shall be added and specified. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
5 | Page 10, Section 6.3, Current required: |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14
5-1 | What is "Co" in formula, it shall be clarify. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
5-2 | There is conflict between this section and section 6.2 from point of view value of coated current density at maximum operating temperature (mA/m2). It shall be rechecked and modified. (If Required) |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
5-3 | It shall be clarify how to calculate the total current required. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
6 | Page 11, Section 6.5, Ground bed design and resistance: The reference of soil resistivity shall be modified. W-018S is not reference of CP stations that will be installed in GCS and siahmakan gas injection station. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
7 | Page 12, Section 6.5, Ground bed design and resistance: |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14
7-1 | The value of conductor resistivity shall be specified. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
7-2 | It shall be clarified how to calculated "TR I" and "TR V" in table 3. Meanwhile number of anode shall be modified. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
8 | Page 14, Section 6.8, Temporary cathodic protection calculation: What is the reference of 43A current? |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
9 | Page 15, Section 6.8, Temporary cathodic protection calculation: It shall be clarify, what means of "Out of 45, every other 2" in below sentences. The most suitable size of anode will be 60 lbs. So, 14 Anodes, are required as minimum. 15 Test boxes (Out of 45, every other 2) are designed and distribute anodes in 15 points. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
10 | Appendix 7: The Power supply of CP station at Mid-point shall be clarify. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | covered |  |  | Noted and Closed.
11 | Complementary comments will be submitted after received revised document. |  | BK-SUR-ENG-ELE-01-04253 | 2022-05-14 | confirmed |  |  | Noted and Closed.
12 | No Comment. Note 1: It shall be clarify where hase been considered the effect of SRB in calculation. Note 2: Base on the calculation, the ground bed length has been calculated 99m, it shall be rechecked from point of execution view at the beginning and end of pipline. |  | BK-SUR-ENG-ELE-01-06956 | 2023-02-20 | وجود و یا عدم وجود باکتری SRB در محاسبات بی تأثیر است. فقط در انجام Setting ترانس رکتیفایر وجود آن می بایست در نظر گرفته شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 20-Feb-23 |  |  |  |  | Date: