## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0014_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1396 |  |  | Transmital Date: 13/September/2022
Document Title: Mechanical Data Sheets For Slug Catcher |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0109-ME-TR-1396 |  |  | Transmital Date: 13/September/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0014_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اینکه سیال داخل مخزن ترش می باشد لذا استاندارد NACE MR 0175 می بایست در نظر گرفته شود. |  | 1401/2294/325846 | 1401/09/02 | در یادداشت 42 اشاره شده است.
2 | مخرن می بایست دارای Demister Pad باشد. |  | 1401/2294/325846 | 1401/09/02 | در sketch مشخص شده است و در یادداشت 44 اشاره شده است.
3 | سطوح فرآیندی با دیتاشیت فرآیندی در تناقض می باشد. |  | 1401/2294/325846 | 1401/09/02 | با ریویژن 5 مدرک P&ID چک شود.
4 | دلایل حذف یادداشت 11 و 13 و 43 با جزئیات کامل بیان گردد. |  | 1401/2294/325846 | 1401/09/02 | نوت 11 مربوط به ابزار دقیق بوده است که در scope کاری وندور نیست و برای جلوگیری از سردرگمی سازنده تنها اشاره به spec شده است در مراجع و این نوت مطابق آنچه در مابقی دیتاشیت ها انجام شده بود حذف شده است.
نوت 14 تکراری می باشد و در نوت 1 گارانتی عملکرد بر عهده سازنده اشاره شده است. در ضمن این تغییرات در دیتاشبت های قبل نیز اعمال شده بود و کامنتی دریافت نشده بود.
نوت 43 تکراری بود و در نوت 34 به آن اشاره شده بود. به همین دلیل حذف شده است.
5 | با توجه به عدم تغییر متریال دلیل درج نشان ویرایش چه بوده است. |  | 1401/2294/325846 | 1401/09/02 | استاندارد ASTM نیز علاوه بر ASMEII مورد استفاده قرار میگیرد و تغییرات اعمال شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.Naserizadeh |  |  | Clarified By: H.Ghadyani | Signature | M.Fakharian
| Date: 10/19/2022 |  |  |  |  | Date: 09/02/2023