## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-PY-0008_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2061 |  |  | Transmital Date: 02-May-2023
Document Title: Electrical Equipment Arrangement Layout For Switchgear Building of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2061 |  |  | Transmital Date: 02-May-2023
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-PY-0008_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Next revision shall be issued after finalizing or minor comments on architectural drawing for switchgear building of well pads. |  | BK-SUR-ENG-ELE-01-04494 | 2022-05-31 | با توجه به آخرین ویرایش مدرک معماری که با شماره ترنسمیتال 1370 ارسال شده است، این مدرک مورد بازنگری قرار گرفت. لازم به ذکر است هنگام تولید مدرک معماری نظرات بخش برق نیز در این مدرک لحاظ شده است. |  |  | See below item 8.
2 | Dimension and NO. of LV switchgear module, Distribution panels, Capacitor bank, Transformer and etc. shall be finalized according to vendor data base on note 2. (It shall be checked and modified at the stage of receiving technical offer and shall be finalized after PO. by selected vendor documents.) |  | BK-SUR-ENG-ELE-01-04494 | 2022-05-31 | بعد از دریافت پیشنهادات فنی از سازندگان مختلف این مدرک به روزرسانی خواهد شد. |  |  | Will be checked later.
3 | All fuse box shall be shown. |  | BK-SUR-ENG-ELE-01-04494 | 2022-05-31 | اعمال گردید و شماره 11 از جدول تجهیزات به فیوزباکس اختصاص داده شد. |  |  | Noted and Closed.
4 | Front and rear side of switchgears and panels shall be shown by "F" and "R" letters near to switchgears and panels. |  | BK-SUR-ENG-ELE-01-04494 | 2022-05-31 | اعمال گردید. |  |  | See below item 9.
5 | Fan of battery room shall be shown. |  | BK-SUR-ENG-ELE-01-04494 | 2022-05-31 | اعمال گردید و شماره 14 از جدول تجهیزات به فیوزباکس اختصاص داده شد. |  |  | Noted and Closed.
6 | Tag of all equipment shall be added. |  | BK-SUR-ENG-ELE-01-04494 | 2022-05-31 | در جدول تجهیزات تگ نامبر اضافه گردید. |  |  | Noted and Closed.
7 | Complementary comments will be submitted after receiving revised document. |  | BK-SUR-ENG-ELE-01-04494 | 2022-05-31 | در صورتی دریافت کامنت جدید این مدرک به روزرسانی خواهد شد. |  |  | Noted and Closed.
8 | See above item 1: According to electrical comments on architectural drawing for switchgear building of well pads, this document shall be rechecked and modified. (If required) |  | BK-SUR-ENG-ELE-01-05748 | 2022-09-24 | تغییرات اعمال گشت |  |  | Noted and Closed.
9 | See above item 4: Front and rear side of all panels shall be shown. It is important to install charger, capacitor bank and VFD panel(s). |  | BK-SUR-ENG-ELE-01-05748 | 2022-09-24 | اعمال گردید. |  |  | Noted and Closed.
10 | No. of fuse box shall be modified. (Two fuse box shall be shown in battery room.) |  | BK-SUR-ENG-ELE-01-05748 | 2022-09-24 | اعمال گردید. |  |  | Noted and Closed.
11 | It seems the installation location of fuse box is very near to battery rack and eyewash. It is recommended to move battery rack in the middle of battery room or revise battry rack calculation and considered two level instead of one level battery rack. |  | BK-SUR-ENG-ELE-01-05748 | 2022-09-24 | فاصله ها بر اساس کامنت کارفرمای محترم تغییر یافت. |  |  | Noted and Closed.
12 | No Comment. Note 1: According to our telephone conversation, the cable route between battery room and LV room trench shall be modified. It shall be considered duct bank and note 4 shall be modified. Note 2: According to PEDCO letter NO. 316 date 1402.01.16, the capacitor bank calculation shall be rechecked and CB shall be deleted if there is not need to capacitor bank. |  | BK-SUR-ENG-ELE-02-07574 | 2023-05-10 | نوت یک: مطابق با صحبت تلفنی در مدرک سیویل نشان دادهع شده است. نوت دو: با توجه به حذف بانک خازنی، این تابلو از روی مدرک برداشته شد.
13 | No Comment. |  | BK-SUR-ENG-ELE-02-07574 | 2023-05-10
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 10-May-23 |  |  |  |  | Date: