## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0013 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2017 |  |  | Transmital Date: 10.Apr.2023
Document Title: P&ID - Gas Compression Dehydration Package |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2017 |  |  | Transmital Date: 10.Apr.2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0013_D06 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با اعمال نظرات ذیل، مدرک مورد تایید می باشد. شایان ذکر است که مطابق شرایط عمومی پیمان فی ما بین و با توجه به مسئولیتهای مالی-قراردادی پیمانکار، مسئولیت بروز هرگونه اشتباه و تناقض، کمبود اسناد و مدارک فنی و اطلاعات تهیه شده از سوی پیمانکار اعم از اینکه از سوی کارفرما تایید شده و یا نشده باشد بر عهده پیمانکار است. |  | BK-SUR-ENG-PCS-02-07474 | 26.Apr.2023 | مورد تایید است.
2 | ارتباط بین PIC-2151 و PIC-2152 از نوع Soft signal باشد. |  | BK-SUR-ENG-PCS-02-07474 | 26.Apr.2023 | اصلاح گردید.
3 | با توجه به تغییرات ایجاد شده در سیستم جمع آوری گازهای خروجی از واحد بازیافت گلایکول، این مورد بر اساس اطلاعات سازنده در نقشه نمایش داده شود |  | BK-SUR-ENG-PCS-02-07474 | 26.Apr.2023 | پس از دریافت اطلاعات از سازنده و در صورت لزوم در نظر گرفتن سیستم جمع آوری گاز های خروجی از واحد بازیافت گلایکول، در مدرک اعمال خواهد شد.
4 | با توجه به درج Note-13، مشخص شود که آیا Partial Stroke برای شیرهای BDV هم لحاظ شده است؟ |  | BK-SUR-ENG-PCS-02-07474 | 26.Apr.2023 | خیر .این موضوع در Spec تنها برای شیرهای ESDV تعریف شده است.
5 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-02-07474 | 26.Apr.2023 | مورد تایید است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: