## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR 1st STAGE GAS AIR COOLERS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | DT | 0003 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
MECHANICAL DATA SHEETS FOR 1st STAGE GAS AIR COOLERS نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  | SEP.2023 |  | AFC |  |  |  | S.Salehi |  |  | M.Fakharian |  | A.M.Mohseni
D03 |  | JAN.2023 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | OCT.2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | JUN. 2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | DEC.2021 |  | IFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-708834
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR 1st STAGE GAS AIR COOLERS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | DT | 0003 |  | D04
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 65
2 | X | X | X |  | X |  | X |  | 66
3 | X | X | X |  | X |  |  |  | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X | [5 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Notes
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR 1st STAGE GAS AIR COOLERS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 5
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME | DT | 0003 | D04
General Notes
| 1. | The Asterisk * denotes information and/or confirmation required from VENDOR.
| 2. | VENDOR shall give tube count of each pass if irregular.
| 3. | Inlet/Outlet nozzles' size and number shall be defined by VENDOR at the same side of aircooler (even pass numbers are allowed).
| 4. | I/P converter & pneumatic actuator for fan blades shall be provided by VENDOR as per P&ID.
| 5. | Hydro Test shall be done for Tube-Side by VENDOR based on ITP. The test procedure shall comply with the code & spec. requirements and
it should be confirmed by CLIENT.
| 6. | 10 % over design on duty / flow rate shall be considered.
| 7. | Half of fans shall be equipped with variable pitch automatic system to control fluid outlet temperature.
| 8. | Electrical motor shall be rated according to project site condition.
| 9. | For LV induction motor the relevant electrical data sheet shall be filled in and submitted by Vendor acc. to IPS-M-EL-131(2) and
"Data Sheets For LV Induction Motors" Doc. No. BK-GCS-PEDCO-120-EL-DT-0008.
| 10. | Ground and bonding facilities shall be provided by Vendor (at least 2 points) on air coolers' structure.
| 11. | Instrument selection, connection & cabling shall be acc. to "Specification For Instrumentation" Doc. No. BK-GNRAL-PEDCO-000-IN-SP-0001
"Specification For Instrument and Control of Package Unit System (PU)" Doc. No. BK-GNRAL-PEDCO-000-IN-SP-0004
"Specification For Instrument/F&G Cables" Doc. No. BK-GNRAL-PEDCO-000-IN-SP-0010
instrumentation design criteria for unit 120
| 12. | Surface preparation & coating shall be acc. to "Specification for Painting" with Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006
| 13. | Allowable nozzle load shall be acc. to "Specification For Air Cooled Heat Exchangers" Doc. No. BK-GCS-PEDCO-120-ME-SP-0001
| 14. | Vendor shall be responsible for mechanical, process and thermal performance of the equipment
| 15. | Bundle to be self draining. The last row should 1% sloped.
| 16. | For maximum, minimum and average temperature, also relative humidity refer to "BK-GNRAL-PEDCO-000-PR-DB-0001".
| 17. | Material requirement should be in compliance with NACE MR 0175/ISO 15156 and Technical Specification for Material Requirements in Sour
service Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0008, IPS-MPM-200
| 18. | Pipe flanges and flanged fittings shall be according to ANSI B16.5, large diameter steel flange shall be according to ANSI B16.47 series A
|  | Flange Material | [5 empty] | Pipe Material
|  | Flange material shall be SA 182 Gr 316L | [5 empty] | Pipe material shall be SA 312 Gr 316L
| 19. | Hazardous classification, all instrumentation and electrical devices shall be acc. To "Hazard Source List"
Doc. No. BK-GCS-PEDCO-120-SA-LI-0001 and "Hazardous Area Classification Layout" Doc. No. BK-GCS-PEDCO-120_SA-PY-0002
| 20. | Air Cooler shall also be checked for Winter Case.
| 21. | The prepared data sheets are for one train.
| 22. | Gasket shall be spiral wound type, graphite filled with inner ring S.S.316 and outer ring S.S 316.
| 23. | All external bolts and nuts shall be hot dip galvanized.
| 24. | Minimum requirement for pre-commissioning, commissioning, start up and two years operation and spare parts shall be in accordance with
document E&C-QC-SP-1.
| 25. | It will be finalized after receiving compressor supplier data.
| 26. | vendor is responsible to provide vibration switch (10A@110VAC rating )suitable for 24 VDC Signal.
The switches shall be EExd, IIB T4 and the weatherproof requirements of IP-65 as per IEC-60529.
•Switch element shall be of the micro switch snap action type Micro-switches shall be two double pole double throw (DPDT) type
•Repeatability shall be ±1% or better of full scale
•The accuracy of the pressure switch assembly shall be at least 1% of the span

## Sheet 1
NISOC | [7 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR 1st STAGE GAS AIR COOLERS
شماره پیمان: | [7 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه |  |  | شماره صفحه: 4 از 5
9184 – 073 - 053 | [7 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | ME |  | DT | 0003 | D04
Mechanical Data Sheets For 1st Stage Gas Air Coolers (AE-2101 A/B/C) / sheet 1 of 2
Rev | DATA SHEET | [27 empty] | Rev
| Plant location |  |  |  | Bushehr (Binak) | [11 empty] | Heat exchanged, (Normal x Overdesign) kW | [6 empty] | 332 x 1.1 (Note 6)
| CLIENT |  |  |  | NISOC | [11 empty] | Surfacec /item-Finned tube, m2 | [6 empty] | *
| Tag No. |  |  |  | AE-2101 A/B/C | [11 empty] | Bare tube, m2 | [6 empty] | *
| No. Req'd |  |  |  | Total |  | 3 |  | Working |  | 2 |  | Standby |  | 1 |  | MTD, eff., °C | [6 empty] | *
| Service |  |  |  | Sour Service | [11 empty] | Transfer rate-finned, W/m2.K | [6 empty] | *
| Type of draught |  |  |  | l | Induced |  |  |  | m | Forced | [5 empty] | Bare tube, service, W/m2.K | [6 empty] | *
| Bay size (W × L) , m |  |  |  | * | [11 empty] | Bare tube, clean, W/m2 | [6 empty] | *
| No. of bays/items |  |  |  | *
Basic Design Data
| Code Requirements |  |  |  | API 661 / ASME Code, Sec. VIII, Div. 1 | [11 empty] | Structural code
| Local Standard |  |  |  | IPS-E-PR-785 / IPS-G-ME-245 | [11 empty] | Flammable service | [7 empty] | l | Yes | m | No
| Tube bundle code stamped | [8 empty] | m | Yes |  | l | No |  |  | Lethal/Toxic service | [7 empty] | m | Yes | l | No
| Heating coil code stamped | [8 empty] | m | Yes |  | l | No |  |  | Sour service | [7 empty] | l | Yes | m | No
| Winterization control | [8 empty] | m | Yes |  | l | No |  |  | Cyclic service | [7 empty] | m | Yes | l | No
| Chemical cleaning | [8 empty] | m | Yes |  | l | No |  |  | Mechanical cleaning | [7 empty] | m | Yes | l | No
Performance Data ─ Tube Side
[23 empty] | In |  |  |  | Out
| Fluid name | [6 empty] | Hydrocarbon | [8 empty] | Line (Pipe) size, in | [5 empty] | 6 |  |  |  | 6
| Total fluid entering, kg/h | [6 empty] | 8664 | [8 empty] | Temperature, °C | [5 empty] | 124.8 (Note25) |  |  |  | 60
| Dew/bubble point, °C | [6 empty] | / | [8 empty] | Total flow rate (liq./vap.), kg/h | [5 empty] | - /8664 |  |  |  | - / 8664
| m | Pour point |  |  |  | m | Freeze point,°C | [9 empty] | Water/Steam, kg/s | [5 empty] | - |  |  |  | -
| Latent heat, KJ/Kg | [15 empty] | Noncondensable, kg/s | [5 empty] | - |  |  |  | -
| Inlet pressure, Barg | [6 empty] | 19 | [8 empty] | Molecular Wt.(cond./vap.) | [5 empty] | - / 24.52 |  |  |  | - / 24.52
| Pressure drop (allow./calc.), Bar | [6 empty] | 0.7 / * | [8 empty] | Density (liq./vap.),kg/m3 | [5 empty] | - / 15.38 |  |  |  | - / 18.28
| Velocity (allow./calc.), m/s | [6 empty] | / * | [8 empty] | Specific heat (liq./vap.),KJ/kg.mol.C | [5 empty] | - / 54.53 |  |  |  | - / 50.54
| Inside foul res., m2.K/W | [6 empty] | 0.0002 | [8 empty] | Thermal concuctivity (liq./vap.), W/m.K | [5 empty] | - / 0.042 |  |  |  | - / 0.033
[17 empty] | Viscosity (liq./vap.), cP | [5 empty] | - / 0.015 |  |  |  | - / 0.013
Performance Data ─ Air Side
| Air inlet temperature, °C | [10 empty] | 50.26 |  |  |  |  | Face velocity, m/s | [9 empty] | *
| Air flow rate/item, (m3/s) | [10 empty] | * |  |  |  |  | Min. ambient air temp.,°C | [9 empty] | 5
| Mass velocity (net free area), kg/s.m2 | [15 empty] | Altitude, m | [9 empty] | 12.5
| Air outlet temperature, °C | [10 empty] | * |  |  |  |  | Static pressure, Bar | [9 empty] | *
| Air flowrate/fan, m3/s | [10 empty] | * |  |  |  |  | Airside foul res., m2.K/W | [9 empty] | 0.00035
Design, Materials & Construction
| Design pressure, Barg | [7 empty] | 22 | [7 empty] | Heating Coil | [6 empty] | m | Yes |  | l | No
| Test pressure, Barg | [7 empty] | Per Code & Spec. Requirements | [7 empty] | No. of tubes | [8 empty] | O.D., mm
| Vaccume pressure | [7 empty] | - | [7 empty] | Tube material
| Design temperature, °C | [7 empty] | 155 | [7 empty] | Fin material and type
| Min. design metal temperature, °C | [7 empty] | -28 | [7 empty] | Thickness, mm
| NACE Requirement | [8 empty] | l | Yes |  |  | m | No |  | Pressure design code |  |  |  |  | ASME Code, Sec. VIII, Div. 1
| HIC / SSC Test Requirements | [8 empty] | m | Yes |  |  | l | No |  | Stamp |  |  |  |  | m | Yes |  | l | No
| Tube bundle | [15 empty] | Heating fluid | [6 empty] | Flowrate, kg/s
| Size (W × L), m |  |  |  |  | (*) | [10 empty] | Temperature (in/out), °C |  |  |  |  | /
| No./bay |  | * |  |  | No. of tube rows | [5 empty] | * |  |  |  |  | Inlet pressure, Bar
| Bundles in parallel |  |  | * |  |  |  |  | In series | [7 empty] | Pressure drop (allow./calc.), Bar |  |  |  |  | /
| Structure mounting |  |  |  | l | Grade |  |  | m | Pipe rack |  |  |  | m | Other |  | Design temp, °C
| Structural material | [7 empty] | SA 36 H.D.G | [7 empty] | Design Press., Bar
| Pipe-rack beams (distance C-C) | [15 empty] | Inlet/Outlet nozzle, DN |  |  |  |  | /
| Ladders, walkways, platforms | [8 empty] | l | Yes |  | m | No |  |  | Header
| Ladders, walkways, platforms material | [7 empty] | SA 36 H.D.G | [7 empty] | Type |  |  |  | Plug
| Structure surf. Prep./coating | [15 empty] | Material |  |  |  | SA 240 Gr 316L
| Header surf. Prep./coating | [15 empty] | Corr. Allow., mm |  |  |  | -
| Tube / Tubesheet Connection |  |  |  |  | Expanded + Strength welded | [10 empty] | No. of passes |  |  |  | (Note 2)
| Bundle Frame |  |  |  |  | H.D.G. | [10 empty] | Radiography |  |  |  | Full (100% RT)
| Vibration Switches |  |  |  |  | Yes (Explosion Proof, 24 VDC, IP 65) | [7 empty] | (Note 26) |  |  | Post Weld Heat Treatment |  |  |  | -
| Steam Coil | [8 empty] | m | Yes |  | l | No
| Recirculation System | [8 empty] | m | Yes |  | l | No
Louver
| Material |  |  |  | SA 283 (H.D.G)
| Action type: | [6 empty] | m | Opposed |  |  |  | m | Parallel
| Action control: | [6 empty] | m | Auto |  |  |  | l | Manual

## Sheet 2
NISOC | [8 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR 1st STAGE GAS AIR COOLERS
شماره پیمان: | [8 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک |  | سریال |  |  | نسخه |  |  | شماره صفحه: 5 از 5
9184 – 073 - 053 | [8 empty] | BK |  | GCS |  | PEDCO |  | 120 | ME |  | DT |  | 0003 |  |  | D04
Mechanical Data Sheets For 1st Stage Gas Air Coolers (AE-2101 A/B/C) / sheet 2 of 2
Rev. | DATA SHEET | [31 empty] | Rev.
| Header (continued) | [15 empty] | No./bundle |  |  |  | * | [5 empty] | Length, (m) |  |  | *
| Slope, mm/m | [5 empty] | * | [9 empty] | Pitch, (mm) |  |  |  | *
| Plug material | [5 empty] | SA 182 Gr. 316L | [9 empty] | Layout
| Gasket material | [5 empty] | * | [9 empty] | Fin
| Nozzle |  |  |  | No. |  | Size, (in) |  |  |  |  | Rating / Facing |  |  |  |  | Type | [6 empty] | *
| Inlet |  | (Note 3) |  | 1* |  | 6 * |  |  |  |  | 300# , R.F. |  |  |  |  | Material | [6 empty] | *
| Outlet |  | (Note 3) |  | 1* |  | 6 * |  |  |  |  | 300# , R.F. |  |  |  |  | Stock thickness, (mm)
| Vent |  |  |  | 1 |  | 2 |  |  |  |  | 300# , R.F. |  |  |  |  | Selection temperature, °C
| Drain |  |  |  | 1 |  | 2 |  |  |  |  | 300# , R.F. |  |  |  |  | O.D. (mm)
| Misc. Conn's TI | [8 empty] | PI | [6 empty] | Fin Density (fin / meter)
| Min. wall thickness (mm) | [15 empty] | Design Code | [6 empty] | ASME Code, Sec. VIII, Div. 1
| Tube | [15 empty] | Customer Specification
| Material |  |  | SA 213 Gr 316L | [12 empty] | P&ID Number | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
| O. D., (mm) |  |  | * | [5 empty] | Min. wall thickness, (mm) |  |  |  |  | *
Mechanical Equipment
| Fan | [15 empty] | Enclosure
| Manufacturer & model | [5 empty] | * | [9 empty] | Volt |  | 400 | [5 empty] | Phase |  | 3 |  |  |  | Cycle | 50 HZ
| No./Bay | [9 empty] | Speed, r/min | [5 empty] | Fan noise level (allow./calc.), dB(a), @ m | [9 empty] | 75 dB @ 15m
| Diameter,m |  |  | * | [6 empty] | No. of blades | [5 empty] | Fan max. sound pressure level | [9 empty] | 85 dBA
| Angle, Degrees | [15 empty] | Fan Area Classification | [10 empty] | Zone 2, IIB, T3 (Note 19)
| Pitch adjustment: |  |  |  |  | m | Manual |  |  |  |  | l | Auto |  | (Note 4 & 7) |  | Speed reducer
| Blade material |  |  |  | Aluminum (ASTM B179) | [5 empty] | Hub material | [5 empty] | Type |  |  | *
| kW/ fan. @ des. temp. | [8 empty] | @ min. amb. temp. | [6 empty] | Manufacturer & model | [7 empty] | *
| Max. allow. / calc. tip speed, m/s | [8 empty] | / | [6 empty] | No./bay
| Driver | [15 empty] | Service factor | [9 empty] | Speed ratio
| Type |  |  | Electric Motor | [12 empty] | Support: | [5 empty] | l | Structure |  |  |  |  | m | Pedestal
| Manufacturer, model & Installation type | [8 empty] | * | [6 empty] | Vib. Switch: | [5 empty] | l | Yes (Eexd,IIB,T4) |  |  |  |  | m | No
| No./bay | [7 empty] | Driver kW |  |  |  | * |  |  |  | Enclosure
| Speed, r/min | [8 empty] | Service factor
Controls - Air Side
| Air recirculation: |  |  |  |  | m | None |  |  | m | Internal |  |  | m | External |  | Louvres: | [5 empty] | m | Inlet |  |  | m | Outlet |  | m | Bypass
| Over: |  |  |  |  | m | Slide |  |  | m | End | [5 empty] | Positioner: | [5 empty] | m | Yes |  |  | m | No
| Degree control of outlet process temp. | [15 empty] | Signal air pressure, Barg
| (max. cooling), +/- °C | [5 empty] | / | [9 empty] | From | [9 empty] | To
| Action on control signal failure | [15 empty] | From | [9 empty] | To
| Fan pitch: |  |  |  |  | m | Minimum |  |  | m | Maximum |  |  | m | Lockup |  | Supply air pressure, Barg
| Louvres: |  |  |  |  | m | Open |  |  | m | Close |  |  | m | Lockup |  | Max. | [9 empty] | Min.
| Actuator air supply | [15 empty] | Max. | [9 empty] | Min.
| Fan: |  |  |  |  | m | None |  |  | m | Positioner |  |  | m | Bias relay
Shipping
| Plot area (W × L), m |  |  |  |  | * | [10 empty] | Total , kg |  |  |  |  | *
| Bundle mass, kg |  |  |  |  | * | [10 empty] | Shipping, kg |  |  |  |  | *
| Bay, kg |  |  |  |  | *
Winter Case
| Fluid name | [7 empty] | Hydrocarbon | [7 empty] | Temperature, °C | [8 empty] | 113.1 |  |  |  | 60
| Total fluid entering, kg/h | [7 empty] | 7585 | [7 empty] | Total flow rate (liq./vap.), kg/h | [8 empty] | - / 7585 |  |  |  | - /7585
| Dew/bubble point, °C | [7 empty] | / | [7 empty] | Water/Steam, kg/s | [8 empty] | - |  |  |  | -
| m | Pour point |  |  |  |  | m | Freeze point,°C | [8 empty] | Noncondensable, kg/s | [8 empty] | - |  |  |  | -
| Latent heat, KJ/Kg | [15 empty] | Molecular Wt.(cond./vap.) | [8 empty] | - / 21.56 |  |  |  | - / 21.56
| Inlet pressure, Barg | [7 empty] | 19 | [7 empty] | Density (liq./vap.),kg/m3 | [8 empty] | - / 13.85 |  |  |  | - / 15.81
| Pressure drop (allow./calc.), Bar | [7 empty] | 0.7 / * | [7 empty] | Specific heat (liq./vap.),KJ/kg.mol.C | [8 empty] | - / 48.4 |  |  |  | - / 45.63
| Velocity (allow./calc.), m/s | [7 empty] | / * | [7 empty] | Thermal concuctivity (liq./vap.), W/m.K | [8 empty] | - / 0.042 |  |  |  | - / 0.035
| Inside foul res., m2.K/W | [7 empty] | 0.0002 | [7 empty] | Viscosity (liq./vap.), cP | [8 empty] | - / 0.014 |  |  |  | - / 0.013