## Cover
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
PANEL & JUNCTION BOX LIST
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 1 از 5
053 – 073 - 9184 |  | BK | GCS | PEDCO | 120 | IN | LI | 0005 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
PANEL & JUNCTION BOX LIST نگهداشت و افزایش تولید میدان نفتی بینک
D03 | SEP.2023 | IFA |  |  | P.Hajisadeghi |  | M.Fakharian |  | S.Faramarzpour
D02 | DEC.2022 | IFA |  |  | P.Hajisadeghi |  | M.Fakharian |  | M.Mehrshad
D01 | JUNE.2022 | IFA |  |  | P.Hajisadeghi |  | M.Fakharian |  | M.Mehrshad
D00 | FEB.2022 | IFC |  |  | P.Hajisadeghi |  | M.Fakharian |  | M.Mehrshad
Rev. | Date | Purpose of Issue / Status |  |  | Prepared by: |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  | CLIENT Doc. Number:F0Z-708971
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Revisions
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
PANEL & JUNCTION BOX LIST
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 2 از5
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0005 | D03
REVISION RECORD SHEET
| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04
| 1 | X | X | X | X |  |  | 41
| 2 | X | X | X | X |  |  | 42
| 3 | X | X | X | X |  |  | 43
| 4 | X | X | X | X |  |  | 44
| 5 | X | X | X | X |  |  | 45
| 6 |  |  | X | X |  |  | 46
| 7 |  |  | X | X |  |  | 47
| 8 | [6 empty] | 48
| 9 | [6 empty] | 49
| 10 | [6 empty] | 50
| 11 | [6 empty] | 51
| 12 | [6 empty] | 52
| 13 | [6 empty] | 53
| 14 | [6 empty] | 54
| 15 | [6 empty] | 55
| 16 | [6 empty] | 56
| 17 | [6 empty] | 57
| 18 | [6 empty] | 58
| 19 | [6 empty] | 59
| 20 | [6 empty] | 60
| 21 | [6 empty] | 61
| 22 | [6 empty] | 62
| 23 | [6 empty] | 63
| 24 | [6 empty] | 64
| 25 | [6 empty] | 65
| 26 | [6 empty] | 66
| 27 | [6 empty] | 67
| 28 | [6 empty] | 68
| 29 | [6 empty] | 69
| 30 | [6 empty] | 70
| 31 | [6 empty] | 71
| 32 | [6 empty] | 72
| 33 | [6 empty] | 73
| 34 | [6 empty] | 74
| 35 | [6 empty] | 75
| 36 | [6 empty] | 76
| 37 | [6 empty] | 77
| 38 | [6 empty] | 78
| 39 | [6 empty] | 79
| 40 | [6 empty] | 80

## Notes
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
PANEL & JUNCTION BOX LIST
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 5
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0005 | D03
CONTROL PANELS LIST
CONTROL PANELS LIST
| ITEM | TAG | DESCRIPTION | LOCATION | REFERENCE DOC. | CPU TYPE | I/O CHANNEL QTY. |  |  |  | REMARK | REVISION
[7 empty] | AI | AO | DI | DO
| 1 | DCS-1001 | DCS PANELS | Technical room | BK-GCS-PEDCO-120-IN-PY-0001 | * | 100 | 15 | 190 | 110 | This panel is included communication ports
| 2 | ESD-1001 | ESD PANELS | Technical room | BK-GCS-PEDCO-120-IN-PY-0001 | * | 72 | 0 | 56 | 110 | This panel is included communication ports
| 3 | F&G-1001 | f&g PANELS | Technical room | BK-GCS-PEDCO-120-IN-PY-0001 | * | 106 | 0 | 57 | 156 | This panel is included communication ports
| 4 | UCP -A | COMPRESSORS PANEL(SYSTEM AND MARSHALLING) | Technical room | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 5 | UCP -B | COMPRESSORS PANEL(SYSTEM AND MARSHALLING) | Technical room | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 6 | UCP -C | COMPRESSORS PANEL(SYSTEM AND MARSHALLING) | Technical room | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 7 | HVAC | HAVC | Technical room | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 8 | F&G Mimic panel | mimic panel | TECHNICAL ROOM | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | 69 | BY VENDOR
| 9 | ESD Console | Console | TECHNICAL ROOM | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | 17 | 11 | BY VENDOR
| 10 | LCP-C-2203A | Air Compressor PK. | TECHNICAL ROOM | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 11 | LCP-C-2203B | Air Compressor PK. | TECHNICAL ROOM | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 12 | UCP-G-2204 | NITROGEN PK. | TECHNICAL ROOM | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 13 | LCP-PK-2207 | CORROSION INHIBITOR PK | FIELD | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 14 | LCP-IG-2201 | IGNITION CONTROL PANEL | FIELD | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 15 | LCP-PK-2208 | Methanol Injection PANEL | FIELD | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 16 | LCP-DR-2203 | Air Dryer PK. | FIELD | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 17 | LCP-P-2301A | Fire Water Pump Package | FIELD | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 18 | LCP-P-2301B | Fire Water Pump Package | FIELD | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 19 | LCP-P-2302A | Fire Water Pump Package | FIELD | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 20 | LCP-P-2302B | Fire Water Pump Package | FIELD | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 21 | FACP | FIRE ALAM CONTROL PANEL | TECHNICAL ROOM | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 22 | CO2 PANEL | TOTAL FLOODING SYSYEM | SUBSTATION BUILDING | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
| 23 | PA/GA PANEL | PAGING AND ALARM PANEL | CONTROL ROOM | BK-GCS-PEDCO-120-IN-PY-0001 | * | * | * | * | * | BY VENDOR
Reference Document :
| 1 | BK-GCS-PEDCO-120-IN-LI-0002 IO LIST FOR CONTROL SYSTEM
| 2 | BK-GCS-PEDCO-120-IN-LI-0003 IO LIST FOR ESD SYSTEM
| 3. | BK-GCS-PEDCO-120-IN-LI-0004 IO LIST FOR F&G SYSTEM
| 4 | BK-GNRAL-PEDCO-000-IN-SP-0010 SPECIFICATION FOR INSTRUMENT & F&G CABLES
| 5 | BK-GCS-PEDCO-120-IN-DG-0008 NSTRUMENT & F&G JUNCTION BOX TERMINATION DIAGRAM
D03
D03
D03

## LIST
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
PANEL & JUNCTION BOX LIST
شماره پیمان : |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0005 | D03
JUNCTION BOXES LIST
ITEM | TAG | JB SIGNALS TO | INPUT CABLE ENTRY NO.* SIZE |  | INPUT CABLE PLUG NO.* SIZE | OUTPUT CABLE ENTRY NO.* SIZE | OUTPUT CABLE PLUG NO.* SIZE |  | OUTPUT CABLE | PAIR/ CORE /TRAID | TERMINAL NO.s | ELECT. PROT. | AREA CLASSIFICATION | BOX SIZING (BY VENDOR) | REMARK | REVISION
1 | JBD-A-2101 | DCS-1001 | 4*M20 |  | 8*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
2 | JBD-A-2102 | DCS-1001 | 9*M20 |  | 3*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
3 | JBD-A-2103 | DCS-1001 | 12*M20 |  | 7*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
4 | JBD-A-2104 | DCS-1001 | 14*M20 |  | 5*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
5 | JBD-A-2105 | DCS-1001 | 14*M20 |  | 5*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
6 | JBD-A-2106 | DCS-1001 | 14*M20 |  | 5*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
7 | JBD-A-2107 | DCS-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
8 | JBD-A-2108 | DCS-1001 | 7*M20 |  | 5*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
9 | JBD-A-2109 | DCS-1001 | 8*M20 |  | 4*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
10 | JBD-A-2110 | DCS-1001 | 4*M20 |  | 8*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
11 | JBD-A-2111 | DCS-1001 | 2*M20 |  | 10*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
12 | JBD-D-2101 | DCS-1001 | 2*M20 |  | 10*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
13 | JBD-D-2102 | DCS-1001 | 10*M20 |  | 9*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
14 | JBD-D-2103 | DCS-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
15 | JBD-D-2104 | DCS-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
16 | JBD-D-2105 | DCS-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
17 | JBD-D-2106 | DCS-1001 | 12*M20 |  | 7*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
18 | JBD-D-2107 | DCS-1001 | 3*M20 |  | 4*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
19 | JBD-S-2101 | DCS-1001 | 3*M20 |  | 4*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
20 | JBD-S-2102 | ESD-1001 | 2*M20 |  | 5*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
21 | JBD-S-2103 | ESD-1001 | 2*M20 |  | 5*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
22 | JBD-S-2104 | ESD-1001 | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
23 | LCP-IG-2201 | ESD-1001 | 9*M20 |  | 14*M20 | 12*M40 | 2*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
24 | LCP-PK-2207 | ESD-1001 | 12*M20 |  | 7*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
25 | JBE-A-2101 | ESD-1001 | 11*M20 |  | 8*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
26 | JBE-A-2102 | ESD-1001 | 10*M20 |  | 9*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
27 | JBE-A-2103 | ESD-1001 | 10*M20 |  | 9*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
28 | JBE-A-2104 | ESD-1001 | 11*M20 |  | 8*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
29 | JBE-A-2105 | ESD-1001 | 4*M20 |  | 8*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
30 | JBE-A-2106 | ESD-1001 | 8*M20 |  | 4*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
31 | JBE-A-2107 | ESD-1001 | 5*M20 |  | 7*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
32 | JBE-D-2101 | F&G-1001 | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | TRAID | 29 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
33 | JBE-D-2102 | F&G-1001 | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | TRAID | 29 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
34 | JBE-D-2103 | F&G-1001 | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | TRAID | 29 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
35 | JBE-S-2101 | F&G-1001 | 2*M20 |  | 10*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
36 | JBE-S-2102 | F&G-1001 | 5*M20 |  | 7*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
37 | JBE-S-2103 | F&G-1001 | 7*M20 |  | 5*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
38 | JBE-S-2104 | F&G-1001 | 7*M20 |  | 5*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
39 | JBE-S-2105 | F&G-1001 | 7*M20 |  | 5*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
40 | JBE-S-2106 |  | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
41 | JBE-S-2107 | F&G-1001 | 2*M20 |  | 10*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | SAFE AREA | BY VENDOR | Note 1 | D03
42 | JBF-A-2101 | F&G-1001 | 9*M20 |  | 3*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | SAFE AREA | BY VENDOR | Note 1 | D03
43 | JBF-A-2102 | F&G-1001 | 7*M20 |  | 5*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
44 | JBF-A-2103 | F&G-1001 | 8*M20 |  | 4*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
45 | JBF-A-2104 | F&G-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
46 | JBF-A-2105 | F&G-1001 | 8*M20 |  | 4*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
47 | JBF-A-2106 | F&G-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
48 | JBF-A-2107 | F&G-1001 | 8*M20 |  | 4*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
49 | JBF-A-2108 | F&G-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
50 | JBF-A-2109 | F&G-1001 | 5*M20 |  | 7*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
51 | JBF-A-2110 | F&G-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
52 | JBF-A-2111 | F&G-1001 | 3*M20 |  | 9*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
53 | JBF-A-2112 | F&G-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
54 | JBF-A-2113 | F&G-1001 | 6*M20 |  | 6*M20 | 1*M40 | 1*M40 |  | 12 | TRAID | 49 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
55 | JBF-A-2114 | F&G-1001 | 3*M20 |  | 7*M20 | 1*M32 | 1*M32 |  | 7 | TRAID | 29 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
56 | JBF-D-2101 | F&G-1001 | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
57 | JBF-D-2102 | F&G-1001 | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
58 | JBF-D-2103 | F&G-1001 | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
59 | JBF-D-2104 | UCP-A | 6*M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
60 | JBF-D-2105 | UCP-B | 2*M20 |  | 5*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
61 | JBF-D-2106 | UCP-C | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
62 | JBF-D-2108 | UCP-B | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
63 | JBF-D-2109 | UCP-C | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
64 | JBF-D-2110 | UCP-A | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
65 | JBF-D-2111 | UCP-B | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
66 | JBF-D-2112 | UCP-C | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
67 | JBF-D-2113 | UCP-B | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
68 | JBF-D-2114 | UCP-C | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
69 | JBF-D-2115 | UCP-A | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
70 | JBF-D-2116 | UCP-B | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
71 | JBF-D-2117 | UCP-C | 1*M25 & 3 M20 |  | 1*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
72 | JBU-A-2101 |  | 12*M20 |  | 7*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
73 | JBU-A-2102 |  | 12*M20 |  | 7*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
74 | JBU-A-2103 |  | 12*M20 |  | 7*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
75 | JBU-A-2104 |  | 3*M20 |  | 9*M20 | 1*M40 | 1*M40 |  | 12 | PAIR | 37 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
76 | JBU-D-2101 |  | 12*M20 |  | 7*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
77 | JBU-D-2102 |  | 10*M20 |  | 9*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
78 | JBU-D-2103 |  | 10*M20 |  | 9*M20 | 1*M50 | 1*M50 |  | 19 | PAIR | 58 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
79 | JBU-S-2101 |  | 5*M20 |  | 2*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
80 | JBU-S-2102 |  | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
81 | JBU-S-2103 |  | 4*M20 |  | 3*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
82 | LCP-P-2301A |  | 5*M20 |  | 2*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
83 | LCP-P-2301B |  | 5*M20 |  | 2*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
84 | LCP-P-2302A |  | 5*M20 |  | 2*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
85 | LCP-P-2302B |  | 5*M20 |  | 2*M20 | 1*M32 | 1*M32 |  | 7 | PAIR | 22 | Eex " E " | ZONE 2 | BY VENDOR | Note 1 | D03
1 - 1-Plug and Gland size shall be finlized based on the approved vendo cable data sheet.
D03
TOTALLY REVIZED