## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LI-0005_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2101 |  |  | Transmital Date: 14-May-2023
Document Title: Electrical I/O Signal List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0202-EL-TR-2101 |  |  | Transmital Date: 14-May-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-LI-0005_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as AFC after finalizing or minor comments on below prerequisite documents: -I/O List for control system -I/O List for ESD system -P&ID document base on HAZOP study. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید. |  |  | Noted and Closed.
2 | The signals between DCS (IRP) and MV/LV switchgears incomings, Coupling and outgoing feeders, AC/DC UPS, generator Control panel, Transformers alarm window, packages control panel, etc shall be added to list. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید. |  |  | Noted and Closed.
3 | The signals between RCP and MV switchgear incomings, Coupling and outgoings shall be added to list. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید. |  |  | Noted and Closed.
4 | Type of Output/Input signals (DO/DI/AO/AI), type of connection (Hardwire/Serial Link) and type of signals (Dry/Wet) shall be added and specified. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | با توجه به اینکه ماهیت تابلوی IRP استفاده از منابع تغذیه جدا برای کنتاکتها می باشد لذا تمامی کنتاکتها خشک بوده و کنتاکت WET استفاده نمی شود. |  |  | Noted and Closed.
5 | The electrical I/O list is for signals between MV/LV switchgears (Incoming, Coupling and outgoing feeders), etc. and IRP panel, so columns "from" and "to" shall be modified. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید. |  |  | Noted and Closed.
6 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11
6-1 | Signal between F&G and DC&AC UPS as title "Inhibit to Boost" and "Battery Fan" shall be modified. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | اعمال گردید. |  |  | Noted and Closed.
6-2 | Stop/Start command shall be added for 11/3.3 KV SWGR-Transformer Feeder-Q4 between RCP and MV switchgear. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | اعمال گردید. |  |  | Noted and Closed.
6-3 | Connection points between RCP and MV spare feeders shall be added. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | اعمال گردید. |  |  | Noted and Closed.
7 | signals related to UPS and Chargers shall be finalized based on manufacturer data. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | همانطور که در مدرک SLD مربوط به UPS نشان داده شده است، سازنده موظف است سیگنالهای مرود نیاز را لحاظ نماید. |  |  | Noted and Closed.
8 | As per diesel oil system P&ID, remote stop command from DCS is not required for diesel oil pump, P-2206. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | اعمال گردید. |  |  | Noted and Closed.
9 | As per Glycol Sump Drum P&ID, ESD trip is required for glycol sump pump, P-2104. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | کامنت وارد هست. باید در نقشه Typical فیدر موتور مربوطه، این موضوع در نظر گرفته شود. در مدرک ESD I/O List وجود دارد. |  |  | Noted and Closed.
10 | regarding close drain P&ID, it seems remote start is required for P-2202A/B and P-2203A/B. it shall be rechecked by Process and modified if required. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | سیگنال Start برای پمپ های P-2202 و P-2203 باید اضافه شود. بدیهی است در طراحی تابلوی برق (فیدر موتور)، توسط پیمانکار مربوطه، Start Command باید وجود داشته باشد. |  |  | Noted and Closed.
11 | regarding LP flare system, P&ID, it seems remote start is required for P-2201A/B. it shall be rechecked by Process and modified if required. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | مطابق پاسخ آیتم شماره 10: سیگنال Start برای پمپ های P-2201 باید اضافه شود. بدیهی است در طراحی تابلوی برق (فیدر موتور)، توسط پیمانکار مربوطه، Start Command باید وجود داشته باشد. |  |  | Noted and Closed.
12 | Regarding Gas Compression Dehydration Package P&ID, lean glycol pumps signals shall be added to signal list. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | در I/O List ، سیگنالها مطابق P&ID دیده شده اند: سیگنال پمپهای 2103 با Tag Number های 2161 وجود دارند. |  |  | Noted and Closed.
13 | Signal between MCC and packages LCP shall be added to this document as per manufacturer documents. (for example some signals have been shown in the corrosion inhibitor package P&ID. ) |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | سیگنالهای بین MCC و پکیج بعد از نهایی شدن وندور و تعیین لیست سیگنال توسط سازنده در نظر گرفته خواهد شد. |  |  | Will be checked later.
14 | Instrument Comment: پيرو جلسه مورخ 08/09/1401 با حضور ذينفع اصلي و پيمانكار (صورتجلسه به پيوست آمده است) مقرر گرديد سيگنالهاي مرتبط با ESD كمپرسور از طريق IRP نيز ديده شود،لذا موارد بايستي در مدارك مرتبط بررسي و شفاف سازي شود. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | سیگنالهای کمپرسور بعد از تعیین توسط سازنده مشخص خواهد شد و در تابلوی LV مربوط به بارهای Auxilary لحاظ خواهد شد. |  |  | See below item 16~19
15 | Electrical Comment: No Comment. Note: A separate row shall be added for the serail link connection between MV and LV switchgear protection relay and DCS. |  | BK-SUR-ENG-ELE-02-07713 | 2023-05-27 | برای ورودی های LV در نظر گرفته شده است. ولی از آنجا که مطابق با شرح کار، ورودی های MV در پروژه نمی باشد، لذا نیازی به درنظر گرفتن ارتباط بین تابلوی MV و سیستم DCS نمی باشد.
16 | See above item 14: Instrument Comment: پيشنهاد مي گردد كه شماره مدرك P&ID در فرمت مدرك (جدول) درج گردد. |  | BK-SUR-ENG-ELE-02-07713 | 2023-05-27 | در صفحه دوم به تمامی مراجع مرتبط اشاره شده است.
17 | See above item 14: Instrument Comment: در قالب يك Note قيد گردد كه سيگنالها Redundant و Intrinsically safe نيستند. |  | BK-SUR-ENG-ELE-02-07713 | 2023-05-27 | اعمال گردید.
18 | See above item 14: Instrument Comment: سيگنالهاي خطاي UPS 110Vac به دو دسته General fault و UPS Failure دسته بندي شوند. سيگنالهاي general fault فقط منجر به آلارم در سيستم كنترل شوند و سيگنال UPS failure (براي مثال inverter failure) منجر به صدور ESD 0 شود. |  | BK-SUR-ENG-ELE-02-07713 | 2023-05-27 | این سیگنالها بر اساس کامنتهای بخش برق آن شرکت محترم در مدرک های مرتبط دیاگرام تک خطی و محاسبات در نظر گرفته شده و نهایتا در این مدرک نیز منعکس شده است.
19 | See above item 14: Instrument Comment: تمامي ارتباطات و كنترل از طريق سيستم كنترل/ قطع اضطراري مركزي ايستگاه یا UCP خواهد بود. براي مثال ارتباط مستقيم سيگنال Inhibit to boost (off) و HVAC Fan (Ctrl) قابل قبول نیست و باید اصلاح گردد. |  | BK-SUR-ENG-ELE-02-07713 | 2023-05-27
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 27-May-23 |  |  |  |  | Date: