## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W0075-PEDCO-110-HV-PY-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1512 |  |  | Transmital Date: 10/18/2022
Document Title: Plumbing & Sewage Piping Layout For Switchgear Building - W0075 |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-1512 |  |  | Transmital Date: 10/18/2022
[5 empty] | CRS No: NISOC-CRS-BK-W0075-PEDCO-110-HV-PY-0003_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در نقشه آبرسانی چنانچه در اتاق باتری دوش اضطراری (EMERGENCY SHOWER)وجود دارد طبق بند 6-6-2 استاندارد IPS-G-SF340، قطر لوله آبرسانی به 2 اینچ تغییر یابد. |  | 01/2294/454460 | 2023-02-19 | انجام شد.
2 | عنوان نقشه مطابق نقشه طراحی شده اصلاح گردد. |  | 01/2294/454460 | 2023-02-19 | انجام شد.
3 | استاندارد نقشه کشی در خصوص ضخامت خطوط و سیمبل ها رعایت نگردیده و می بایست اصلاح گردد. |  | 01/2294/454460 | 2023-02-19 | انجام شد.
4 | حجم ابعاد سپتیک اتاق باطری مشخص گردد. |  | 01/2294/454460 | 2023-02-19 | مرجع ابعاد و مشخصات چاله جمع آوری فاضلاب اتاق باتری در مدرک مربوطه اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: