## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-HV-CN-0001_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1890 |  |  | Transmital Date: 2/21/2023
Document Title: HVAC Calculation Note For Switchgear Building - W007S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-HV-TR-1890 |  |  | Transmital Date: 2/21/2023
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-HV-CN-0001_D02 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | دمای اتاق باتری می بایست 24 سانتیگراد در نظر گرفته شود، و در محاسبات لحاظ گردد (بر اساس استاندارد IPS-E-AR-160) |  | 02/2294/19777 | 2023-04-11 | یک دستگاه اسپلیت یونیت دیواری برای اتاق باتری در نظر گرفته شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: