## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-HV-CN-0001_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1890 |  |  | Transmital Date: 2/21/2023
Document Title: HVAC Calculation Note For Switchgear Building - W007S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-HV-TR-1890 |  |  | Transmital Date: 2/21/2023
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-HV-CN-0001_D02 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در خصوص اتاق باتري مطابق بند 3 صورت جلسه ناريخ 10/12/1401 در دفتر شركت توسعه پتروايران اقدام شود |  | BK-SUR-ENG-HVC-01-07065 | 2023-03-01 | Split unit considered for battery room.
2 | 100% reduandancy for HVAC systems inside battery room shall be considered including exhaust fan, cooling system... |  | BK-SUR-ENG-HVC-01-07065 | 2023-03-01 | Based on the project description, a exhaust fan and a split unit considered. The battery room will equipped with a Ni-Ca battery, and the content contained in the standard (100% reduandancy for HVAC systems) is not related to this type of battery.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature | H.naserizadeh |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: