## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-HV-PY-0001_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1441 |  |  | Transmital Date: 9/26/2022
Document Title: HVAC System Layout For Switchgear Building - W007S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-HV-TR-1441 |  |  | Transmital Date: 9/26/2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-HV-PY-0001_D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
| indoor temperature for battery room shall condition (T=250C) |  | BK-SUR-ENG-HVC-01-05780 | 2022-05-07 | According to the design criteria doc. The indoor design temperature of This place is not controled. And too client has no comment about battery room control temprature. this item will be cost impact because air chang is 10 and ambient humidity is high. |  |  | this has mentioned in NIOEC SP-1 and ASHRAE handbook pages also in our comments for design criteria (see attachments)
| this has mentioned in NIOEC SP-1 and ASHRAE handbook pages also in our comments for design criteria (see attachments) |  | BK-SUR-ENG-HVC-01-05780 | 2022-10-02 | Based on NIOEC SP-1 and ASHRAE handbook "Battery rooms should be maintained between approximately 21°C and 27°C for optimum battery capacity and service life". Split unit considered for battery room.
| exhaust fan for battery room shall be had 100 % redundancy unit (it means that , two exhaust fan unit shall consider) |  | BK-SUR-ENG-HVC-01-05780 | 2022-05-07 | this item has been not raised by client, and client has not any comment |  |  | this is same as requirements for battery room in control building according to document number BK-GNRAL-PEDCO-000-HV-DC-0001_D01, also as it is mentioned in NIOEC SP-1 and ASHRAE handbook pages (see attachments)
| this is same as requirements for battery room in control building according to document number BK-GNRAL-PEDCO-000-HV-DC-0001_D01, also as it is mentioned in NIOEC SP-1 and ASHRAE handbook pages (see attachments) |  | BK-SUR-ENG-HVC-01-05780 | 2022-10-02 | Based on the project description, a exhaust fan considered. The battery room will equipped with a Ni-Ca battery, and the content contained in the standard is not related to this type of battery.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: