## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-MR-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1818 |  |  | Transmital Date: 23-Jan-2023
Document Title: PMR For Existent MV Switchgear Expansion & RCP |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1818 |  |  | Transmital Date: 23-Jan-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-MR-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
EL. Comments.
1 | Item 2, General: Total QTY row for 33KV switchgear shall be rechecked and modified. Consideration shall be given that only some cells will be added to existing 33KV switchgear. Meanwhile rated current and capacity of 3.3KV and MV capacitor bank shall be added to description. |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05 | یک نوت جدید برای تکفیک نیازمندی های پروژه اضافه گردید.
2 | "LV/MCC" words shall be modified on all pages base on scope of work and supply. |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05 | اعمال گردید.
3 | Following documents shall be added as reference documents in section 11.1 LIST OF REFERENCE / APPLICABLE DOCUMENTS: -Data Sheets For Remote Control Panel -Wiring Diagram For Interposing Relay Panel (IRP) -Electrical Overall Single Line Diagram -Specification For Painting -Document Numbering Procedure |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05 | 1- داده برگه کنترل اضافه گردید. 2- نیازی به اضافه کردن مدرک IRP نمی باشد. 3- اضافه کردن مدرک تک خطی, باعث ایجاد ابهام و تناقض برای سازنده خواهد شد. 4- دو مدرک دیگر اضافه گردید.
4 | Electrical documents consist of following documents shall be added to Att-1 "Vendor document min. Requirements" - Single line diagram - Schematic Diagrams - Wiring Diagram - Termination Diagram - switchgears/Panel layout arrangement - heat dissipation schedule - Switchgear / Panel foot print - gland plate drawing - Alarm and set point list for protection relays |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05 | اعمال گردید.
5 | Single line diagram for capacitor banks of well pads is not reference document for this document and shall be modified. |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05 | حذف گردید.
6 | In case of any changes in prerequisite documents, this document shall be revised. |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05
QC. Comments.
1 | در بند 6 عبارت "QC Plan" به "ITP" تغيير يابد. |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05 | اعمال گردید.
2 | لزوم ارائه مدارك ITP, QCP, MPS توسط سازنده قبل از برگزاري جلسه PIM در مدرك درج گردد. |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05 | مدارک ذکر شده، همگی جز پیوست های قرارداد می باشد که به هنگام عقد قراداد با برنده مناقصه، منظور خواهد شد. لذا جهت یکپارچگی بین تمامی MR ها از آوردن آنها صرف نظر شده است.
3 | در جدول Attachments 2 (Vendor Documents Minimum Requirements): 1. مدارك SAT Procedure, Final Data Book اضافه گردد. 2. در انتهاي جدول در قسمت نوتها، عبارت "List of Documents will be Finalized in Vendor Document Index and Schedule" به عنوان نوت اضافه گردد. |  | BK-SUR-ENG-ELE-01-06885 | 2023-02-05 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: