## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-DG-0007_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1897 |  |  | Transmital Date: 25-Feb-2023
Document Title: Instrument & F&G Junction Box Termination Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1897 |  |  | Transmital Date: 25-Feb-2023
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-IN-DG-0007_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | فایل اصلی ناخوانا می باشد |  | 1401-2294-497387 | 2023-03-11 | مورد بازنگری گردید.
2 | برداشت پیمانکار از مدارک پایه صحیح نبوده و بارها اتصال سیگنالهای کنترل و توقف بسته خطوط لوله 8 و 4 اینچ به سیستم کنترل / توقف جدید از سوی این امور اعلان شده است. تجهیزات توقف / کنترلی جدید در پنل موجود نصب می شوند ( سیستم کنترل / توقف جدید مستقل از سیستم کنترل / توقف ایستگاه سیاهمکان بوده، فقط یک سیگنال توقف کلی از سیستم موجود دریافت می کند. |  | 1401-2294-497387 | 2023-03-11 | در مدرک I/O List For Control /ESD System (BK-PPL-PEDCO-320-IN-LI-0002 ) نسخه D02 در صفحه 6 نوت مربوط به سیگنالهای که به سیستم کنترل موجود در سیاهمکان ارسال می شوند قید شده است (NOTE 2: ALL INPUT/OUTPUT SIGNALS FOR ABOVE ITEMS SHALL BE CONNECTED TO NEW REQUIRED ACCESSORIES INSTALLED ON EXISTING CONVENTIONAL RELAY BASED CONTROL /ESD PANEL OF SIAHMAKAN PLANT .REDUNDANT SIL3 RELAY BASED SHALL BE CONSIDERED FOR ESD SIGNALS.)
3
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: