## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-PY-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1206 |  |  | Transmital Date: 27-Jul-2022
Document Title: Instrument Cable Trench/Route Layout Drawing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1206 |  |  | Transmital Date: 27-Jul-2022
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-IN-PY-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-05408 | 2022-08-10 | ملاحظه گردید
2 | نوت 2 قابل قبول نمي باشد و لزوم اجراي ترنچ جديد يا استفاده از ترنچ موجود در اين مرحله بايد نهايي گردد. |  | BK-SUR-ENG-INS-01-05408 | 2022-08-10 | درخواست کارفرمای محترم اعمال می گردد. ترانشه های ابزاردقیق جدید اجرا می شوند
3 | در مورد رعايت فاصله ايمن با ترنچ هاي موجود ابزار دقيق و برق مطابق استاندارد IPS و مدارك پروژه شفاف سازي صورت پذيرد. |  | BK-SUR-ENG-INS-01-05408 | 2022-08-10 | با توجه به استاندارد IPS حداقل فاصله بین ترانشه برق و ابزاردقیق 30 سانتی متر رعایت شده است
4 | در خصوص كابل كشي در اتاق كنترل موجود شفاف سازي صورت پذيرد؟ از مسير موجود استفاده مي شود يا مسير جديد در نظر گرفته خواهد شد. |  | BK-SUR-ENG-INS-01-05408 | 2022-08-10 | از مسیر موجود بر ای عبور کابل برای اتاق کنترل استفاده می شود
5 | محل نصب JB ها مشخص شود. |  | BK-SUR-ENG-INS-01-05408 | 2022-08-10 | اعمال گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: