## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PH-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1747 |  |  | Transmital Date: 1/1/2023
Document Title: ESD Philosophy |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1747 |  |  | Transmital Date: 1/1/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-PH-0005_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در صفحه 9 از 12، باز شدن ESDV در نظر گرفته شده برای کنارگذر کمپرسورهای مرحله اول، می بایست از اثرات سیستم ESD خارج شده و از سیستم DSC با فرمان و تصمیم اپراتور باز شود. |  | BK-SUR-ENG-PCS-01-06677 | 2023-01-17 | طی آخرین توافقات شیر مذکور از هر دو سیستم فرمان می گیرد.
2 | با توجه به پاسخ ارائه شده توسط پیمانکار به نقطه نظر ذینفع اصلی پروژه در خصوص پذیرش لزوم تخلیه به مشعل در حالت IA Headr Low Low Pressure ، به نظر می رسد که همین استدلال برای Control System Failure نیز صادق باشد. این مورد بررسی و در صورت لزوم در ویرایش بعد اصلاح گردد. |  | BK-SUR-ENG-PCS-01-06677 | 2023-01-17 | سطح ESD-1A برای فعال سازی Failure سیستم کنترل کافی می باشد علت فعالسازی ESD-1A به دلیل افت فشار هوای ابزار دقیق جلوگیری از عدم عملکرد BDV ها در زمان تخلیه می باشد.
3 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-01-06677 | 2023-01-17 | اعمال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: