## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0019 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  |  | OCT.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  |  | MAY.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: F9Z-708939
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0019 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X |  | X |  |  |  | 70
7 |  | X | [6 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0019 | D03
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## Notes
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0019 | D03
GENERAL NOTES:
1- All transmitters shall have output short circuit & reverse polarity protection.
2- Tag plate as per Specification for Instrumentation, shall be stainless steel 304 SS (VTC). Following details shall be engraved on them:
• Tag Number • Range Limit • Service • Manufacture Model
3- Sunshade to be considered for all transmitters.
4- Each transmitter shall have a none-volatile EEprom memory to be used for storing the configuration data and sensor linearization data. This data must be retained in the transmitter to be functional upon power up.
5- Vendor shall identify and detail any deviation from the present instrument datasheet.
6- All transmitters shall be equipped with internal diagnostics software.
7- Push button for span and zero adjustment for all transmitters to be considered by vendor.
8- Indicator scale output configuration for LT tag nos. to be linear.
9- Environmental condition for field instrumentation of Binak oilfield shall be considered as per the following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0

## LT-DP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0019 |  | D03
DATA SHEETS FOR LEVEL TRANSMITTER (DPT TYPE)
GENERAL DATA |  | 1 | Tag No. | [9 empty] | SEE NEXT PAGE
|  | 2 | P & ID No. | [9 empty] | SEE NEXT PAGE
|  | 3 | Equipment No. | [9 empty] | SEE NEXT PAGE
|  | 4 | Area Clacification | [9 empty] | Zone 2, IIB T4
|  | 5 | RFI Protection |  |  |  | Tropicalisation | [5 empty] | NEEDED |  |  | NEEDED
OPERATING CONDITIONS |  | 6 | Fluid | [9 empty] | SEE NEXT PAGE
|  | 7 | Phase | [9 empty] | SEE NEXT PAGE
|  | 8 | Operating Pressure |  |  |  | Design Pressure |  |  |  | (barg) |  | SEE NEXT PAGE |  |  | SEE PAGE 6,7
|  | 9 | Operating Temperature |  |  |  | Design Temperature |  |  |  | (°C) |  | SEE NEXT PAGE |  |  | SEE PAGE 6,7
TRANSMITTER |  | 10 | Element Type | [9 empty] | Differential Pressure
|  | 11 | Process Connection | [9 empty] | SEE NEXT PAGE
|  | 12 | Element Material | [9 empty] | SEE NEXT PAGE
|  | 13 | Enclosure Material | [9 empty] | Die-Cast Aluminium
|  | 14 | Instrument Range | [9 empty] | SEE NEXT PAGE
|  | 15 | Write Protection | [9 empty] | SEE NEXT PAGE (Note 2)
|  | 16 | Power Supply | [9 empty] | 24 VDC-Loop powered
|  | 17 | Output Signal | [9 empty] | (4-20 mA) HART communication protocol
|  | 18 | Electrical Connection | [9 empty] | ISO M20 x 1.5
|  | 19 | Electrical Certification | [9 empty] | Eex ia -IIB T4
|  | 20 | Ingress Protection | [9 empty] | IP-65 as minimum
|  | 21 | Accuracy | [9 empty] | +/- 0.1 % Full Scale
|  | 22 | Repeatability | [9 empty] | +/- 0.1% or better
|  | 23 | Span and Zero Adjustment | [9 empty] | Required
|  | 24 | Over Range Protection | [9 empty] | 1.3 of F.S
DIAPHRAGM SEAL |  | 25 | Type | [9 empty] | N/A
|  | 26 | Size (In) | [9 empty] | N/A
|  | 27 | Fill Fluid | [9 empty] | N/A
|  | 28 | Diaphragm Material | [9 empty] | N/A
|  | 29 | Capillary Material | [9 empty] | N/A
|  | 30 | Instrument Connection | [9 empty] | N/A
|  | 31 | Capillary Length | [9 empty] | N/A
OPTIONS |  | 32 | Integral Indicator | [9 empty] | Required
|  | 33 | Mounting Brackets | [9 empty] | Required, 2" Support Pipe
|  | 34 | Manifold |  |  |  | Body Material | [5 empty] | SEE NEXT PAGE |  |  | 316SS
|  | 35 | Connection | [9 empty] | N/A
|  | 36 | Manifold Model |  |  |  | Manifold Manufacturer | [5 empty] | VTA |  |  | VTA
|  | 37 | Local Indication Requirement | [9 empty] | Required in Digital Display, LCD type
|  | 38 | NACE Requirement |  |  |  | Manufacture | [5 empty] | SEE NEXT PAGE
PURCHASING DATA |  | 39 | Model |  |  |  | Order | [5 empty] | will be finalized later |  | will be finalized later
|  | 40 | Supplier |  |  |  | Manufacturer | [5 empty] | will be finalized later |  | will be finalized later
41
| NOTES : | VTA : VENDOR TO ADVISE
(1) Reference Document: General Specification for Instrumentation "BK-GNRAL-PEDCO-000-IN-SP-0001"
(2) The transmitters which shall be write protected are identified by note 2 in sheet 7. (Also see note 2 in sheet 7)

## LT-DP LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 19 | D03
LEVEL TRANSMITTERS (DPT TYPE) LIST
Item No. | Tag No. | System | P&ID No. | Equipment No. | Fluid | Phase | Design Pressure (barg) | Operating Pressure (barg) | Design Temp. (°C) | Operating Temp. (°C) | Process Connection (Note 4) | Instrument Range (mm) | Element Material | Density (Kg/m3) | Nace | Diaphragm Seal & Capillary Tube Requirement | 5 WAY Manifold/(1/2" NPTx1/2'' NPT)/ TUBE Requirement | Remark
1 | LIT-2111 | DCS | BK-GCS-PEDCO-120-PR-PI-0004-D07 (1 of 2) | V-2104 | HC/WATER | L | F.V/9 | 5.5 | 85 | (15.5 - 32) | 2 x 1/2'' NPT | 4000 | 316 SS | 846 ~ 1012 | YES | NO | YES
2 | LIT-2112 (Note 2) | ESD (SIL 1) | BK-GCS-PEDCO-120-PR-PI-0004-D07 (1 of 2) | V-2104 | HC/WATER | L | F.V/9 | 5.5 | 85 | (15.5 - 32) | 2 x 1/2'' NPT | 4000 | 316 SS | 846 ~ 1012 | YES | NO | YES
3 | LIT-2119 | DCS | BK-GCS-PEDCO-120-PR-PI-0005-D07 | V-2105 | HC/WATER | L | F.V/9 | 5.3 | 85 | (19.23 - 37.17) | 2 x 1/2'' NPT | 1200 | 316 SS | 843 ~ 1012 | YES | NO | YES
4 | LIT-2161 (Note 2) | ESD (SIL a) | BK-GCS-PEDCO-120-PR-PI-0014-D07 | TK-2102 | Lean Glycol | L | FULL OF LIQUID+160mbarg/-7 | 0.1 | 85 | AMB | 2 x 1/2'' NPT | 4200 | 316 SS | 1100 | NO | NO | YES
5 | LIT-2162 | DCS | BK-GCS-PEDCO-120-PR-PI-0014-D07 | TK-2102 | Lean Glycol | L | FULL OF LIQUID+160mbarg/-7 | 0.1 | 85 | AMB | 2 x 1/2'' NPT | 4400 | 316 SS | 1100 | NO | NO | YES
6 | LIT-2221 | DCS | BK-GCS-PEDCO-120-PR-PI-0017-D07 (2 of 2) | V-2202 | HC/WATER | L | F.V/6 | 0.5 | 85 | AMB | 2 x 1/2'' NPT | 2400 | 316 SS | 842.6~ 1012 | YES | NO | YES
7 | LIT-2251 | DCS | BK-GCS-PEDCO-120-PR-PI-0020-D07 (2 of 2) | V-2201 | HC/WATER | L | F.V/6 | 0.5 | 85 | 36 | 2 x 1/2'' NPT | 800 | 316 SS | 843~ 1012 | YES | NO | YES
8 | LIT-2281 | DCS | BK-GCS-PEDCO-120-PR-PI-0023-D07 | V-2206 | Diesel Oil | L | ATM+FULL OF WATER | ATM | 85 | AMB | 2 x 1/2'' NPT | 2200 | 316 SS | 850 | NO | NO | YES | LI-2281 field mounted remote indicator shall be considered by vendor
9 | LIT-2291 | DCS | BK-GCS-PEDCO-120-PR-PI-0024-D06 | TK-2209 | Potable Water | L | ATM+FULL OF WATER | ATM | 85 | AMB | 2 x 1/2'' NPT | 2500 | 316 SS | 1024 | NO | NO | YES | LI-2291 field mounted remote indicator shall be considered by vendor
10 | LIT-2293 | DCS | BK-GCS-PEDCO-120-PR-PI-0025-D07 | V-2107 | Glycol | L | F.V/3.5 | ATM | 85 | AMB | 2 x 1/2'' NPT | 1000 | 316 SS | 1100 | NO | NO | YES
11 | LIT-2301 | DCS | BK-GCS-PEDCO-120-SA-PI-0001-D04 (1 of 2) | TK-2301-A | Fire Water | L | FULL OF WATER | 1 | 85 | AMB | 2 x 1/2'' NPT | 11000 | 316 SS | 1000 | NO | NO | YES
12 | LIT-2302 | DCS | BK-GCS-PEDCO-120-SA-PI-0001-D04 (1 of 2) | TK-2301-B | Fire Water | L | FULL OF WATER | 1 | 85 | AMB | 2 x 1/2'' NPT | 11000 | 316 SS | 1000 | NO | NO | YES
NOTE:
(1) G: GAS L: LIQUID
(2) Transmitters shall be smart type with 4~20 mA HART communication protocol, . If smart type transmitters are selected for ESD application they shall be configured as “write protected”.
(3) Instrument range shall be finalized & filled by vendor.
(4) LT connection to Vessel and required accessories to be considered as per Hook up drawing.
D03