## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0019_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2130 |  |  | Transmital Date:5/21/2023
Document Title: Data Sheets For Diff. Pressure Type Level Transmitter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-2130 |  |  | Transmital Date:5/21/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-DT-0019_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-02-07785 | 2023-05-31 | ملاحظه گردید.
2 | Instrument Range براي LIT-2161 و LIT-2162 مجددا مورد بازنگري قرار گيرد. بنظر مي رسد كه رنج مورد نظر را پوشش نمي دهد. |  | BK-SUR-ENG-INS-02-07785 | 2023-05-31 | اصلاح گردید.
3 | Instrument Range براي LIT-2281 مجددا مورد بازنگري قرار گيرد. بنظر مي رسد كه رنج مورد نظر را پوشش نمي دهد. |  | BK-SUR-ENG-INS-02-07785 | 2023-05-31 | اصلاح گردید.
4 | براي LIT هايي كه قرار است بر روي Ground نمايش داده شود تجهيزات و تمهيدات مورد نياز در نظر گرفته شود. |  | BK-SUR-ENG-INS-02-07785 | 2023-05-31 | ملاحظه می گردد. |  |  | این آیتم بعنوان یک سلول در نظر گرفته شود و برای ترانسمیترهای مرتبط نیز بررسی و اعمال گردد.
D03
1 | با توجه به spec پروژه در خصوص نوت شماره 2 تمامی ترانسمیتر ها می بایست SMART باشند و ترانسمیتر های ESD می بایست write protected باشند. |  | BK-SUR-ENG-INS-02-08449 | 2023-09-13 | اعمال گردید.
2 | مقدار SIL برای ترانسمیترهایی که به سیستم ESD متصل می شوند مطابق نتایج به دست آمده از جلسه SIL مشخص شود. |  | BK-SUR-ENG-INS-02-08449 | 2023-09-13 | اعمال گردید.
3 | با توجه به کامنت داشتن کارفرما و ارسال مدرک AFCُ این مدرک عودت داده می شود و لطفا مدرک با همین ترانسمیتال و شماره مدرک ارسال گردد. |  | BK-SUR-ENG-INS-02-08449 | 2023-09-13 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 13 sep 2023 |  |  |  |  | Date: