## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0023 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2016 |  |  | Transmital Date: 10.Apr.2023
Document Title: P&ID - Diesel Oil System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2016 |  |  | Transmital Date: 10.Apr.2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0023_D06 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | عمومی: سایز شیرهای کنترلی، پس از بررسی محاسبات سازنده نهایی می گردد. |  | 1402/2294/109013 1402/2294/92831 | 1402/03/23 1402/03/09 | مورد تایید است . لازم به ذکر است بند فوق در این مدرک موضوعیت ندارد.
2 | عمومی: برای تجهیزات سطح (Level) مسیرهای Vent و Drain نمایش داده شود. |  | 1402/2294/109013 1402/2294/92831 | 1402/03/23 1402/03/09 | عطف به صورتجلسه مورخ 1402/03/22 در خصوص بررسی و نهایی سازی مدارک مهندسی سطح الارض میدان بینک مقرر گردید ، شیرهای Vent و Drain، برای همه Standpipe ها و LT های از نوع Displacer در مدرک HOOK UP نمایش داده شود.
3 | عمومی: ابعاد و فشار طراحی مخازن مطابق با آخرین ویرایش مدارک محاسباتی مربوطه همسان سازی گردد. |  | 1402/2294/109013 1402/2294/92831 | 1402/03/23 1402/03/09 | ابعاد و فشار طراحی مخازن مطابق با آخرین ویرایش مدارک محاسباتی در نظر گرفته شده است.
4 | در مدرک ارسالی HHLL نسبت به ویرایش قبل تغییر داشته است، ضروریست علت توضیح داده شود. |  | 1402/2294/109013 | 1402/03/23 | رجوع شود به پاسخ بند 2 فوق
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date:

## Sheet3
177500