## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0016 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2019 |  |  | Transmital Date: 11.Apr.2023
Document Title: P&ID - Nitrogen Generation System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2019 |  |  | Transmital Date: 11.Apr.2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-PI-0016_D06 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نقطه نظر پیشین: بخش دوم HAZOP Recommendation شماره 89، در خصوص در نظر گرفتن Trap برای Wet Air KOD به درستی اعمال نشده است. پاسخ پیمانکار مربوط به شماره 90 می باشد. |  | BK-SUR-ENG-PCS-02-07476 | 26.Apr.2023 | اعمال گردید.
2 | کلاس شیر کنترلی می بایست 300# درج گردد. |  | BK-SUR-ENG-PCS-02-07476 | 26.Apr.2023 | اعمال گردید.
3 | نقطه نظر پیشین: Note-9 ویرایش گردد (کلمه Extended) |  | BK-SUR-ENG-PCS-02-07476 | 26.Apr.2023 | اعمال گردید.
4 | نقطه نظر پیشین: MCC و ارتباط آن با UCP، نمایش داده شود. (نظیر آنچه در کمپرسور هوا نشان داده شده). پاسخ پیمانکار قابل قبول نمی باشد. با استدلال ارائه شده دلیل نمایش MCC در بسته کمپرسور هوا که از نوع C می باشد تشریح گردد. |  | BK-SUR-ENG-PCS-02-07476 | 26.Apr.2023 | اعمال گردید.
5 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-02-07476 | 26.Apr.2023 | اعمال می‌گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021