## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0022 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2016 |  |  | Transmital Date: 10.Apr.2023
Document Title: P&ID - Fuel Gas System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2016 |  |  | Transmital Date: 10.Apr.2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0022_D06 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | سایز کلیه نازل های Drum، درج گردد. |  | BK-SUR-ENG-PCS-02-07467 | 24.Apr.2023 | اعمال گردید.
2 | نظر پیشین: تمامی شیرهای با اندازه 2 اینچ و بالاتر از 2 اینچ، می بایست به صورت فلنج نمایش داده شود. به عنوان نمونه شیر قبل از FG-2272. |  | BK-SUR-ENG-PCS-02-07467 | 24.Apr.2023 | اصلاح گردید.
3 | مسیرهای Vent و Drain، برای همه Standpipe ها و LT های از نوع Displacer، در همه نقشه ها به صورت کامل نمایش داده شود. |  | BK-SUR-ENG-PCS-02-07467 | 24.Apr.2023 | عطف به صورتجلسه مورخ 1402/03/22 در خصوص بررسی و نهایی سازی مدارک مهندسی سطح الارض میدان بینک مقرر گردید ، شیرهای Vent و Drain، برای همه Standpipe ها و LT های از نوع Displacer در مدرک HOOK UP نمایش داده شود.
4 | .ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد |  | BK-SUR-ENG-PCS-02-07467 | 24.Apr.2023 | اعمال می‌گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: