## Reply Sheet
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0023_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0753 |  |  | Transmital Date: 12/4/2022
Document Title: Mechanical Data Sheets For Sump Pumps |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0111-ME-TR-0753 |  |  | Transmital Date: 12/4/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-DT-0023_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
| Material shall be at least I-2 |  | BK-SUR-ENG-MEC-01-06937 | 2023-02-15 | Acc. to API-610 (11th Ed.), there is no mandatory requirement for I-2 MATERIAL (considering the pump service). Also Main Client approved the I-1 MATERIAL in previous revisions.
| same as all data sheet, a note shall be added and mentioned min hydro test pressure shall not be less than 24 barg. |  | BK-SUR-ENG-MEC-01-06937 | 2023-02-15 | Hydro test pressure will be considered as per ISO-5199 requirements.
| because of low eff. Of these pumps, the Motor power shall not be less than 4 kw |  | BK-SUR-ENG-MEC-01-06937 | 2023-02-15 | Motor Power will be specified by Vendor (w/ considering all of relevant factors) and submitted to clients for getting written approval (before motor supply).
| The mechanical seal shall be cart. Type, so gland packing in page 5 of 6 shall be mentioned "N.A" |  | BK-SUR-ENG-MEC-01-06937 | 2023-02-15 | The comment is applied.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: S.Zafaresmaeili | Signature | M.Fakharian
| Date: 02/15/2023 |  |  |  |  | Date: 9/23/2023