## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-RT-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1804 |  |  | Transmital Date: 1/17/2023
Document Title: Electrical Network (Load Flow, Motor Starting & Short Circuit) Study Report |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1804 |  |  | Transmital Date: 1/17/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-RT-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطالعات پخش بار و استارت موتورها باید در بدترین حالت (worst case) یعنی تغذیه با یک ترانس انجام شود(بدون در نظر گرفتن خازنها و قرار دادن تپ ترانسها در حالت نرمال ) |  | 1401-2294-444091 | 1401/11/19 | مطالعات شبکه در دو نرم افزار با ویرایش 12.6 و 19 انجام گردید. پخش بار در دو حالت با در نظر گرفتن بانک خازنی و بدون بانک خازنی به پیوست ارائه گردیده است.
2 | جریان اتصال کوتاه steady state باید مد نظر قرار بگیرد. |  | 1401-2294-444091 | 1401/11/19 | مطابق با استاندارد IEC60909به آگاهی می رساند که جریان اتصال کوتاه زیرگذرا می بایست جهت سایزینگ تجهیزات مدنظر قرار گیرد. لذا نیاز به در نظر گرفتن جریان حالت اتصال کوتاه ماندگار نمی باشد.
3 | برای لحاظ نمودن بدترین حالت در MOTOR STARTING باید بزرگترین موتور هر باس استارت شده و فقط یکی از ترانسها در مدار باشد.در ضمن در صورتیکه موتور دوم (معادل آن موتور) با در حالت کار بودن یک موتور استارت می شود باید این موضوع نیز لحاظ شود یعنی موتور های در مدار به عنوان بار لحاظ شوند.(نتیجه می بایست بر روی SLD نیز نمایش داده شود) |  | 1401-2294-444091 | 1401/11/19 | اعمال گردید.
4 | محاسبات پخش بار و اتصال کوتاه در دو حالت نرمال و worst case انجام و نتیجه ی آنها بر SLD نیز نمایش داده شود. |  | 1401-2294-444091 | 1401/11/19 | اعمال گردید.
5 | در حالت نرمال کلیه ترانسها در سرویس و کلیه کوپلر ها باز می باشند. |  | 1401-2294-444091 | 1401/11/19 | اعمال گردید.
6 | در حالت WORST CASE یک ترانس از هر باس در سرویس و کوپلر ها بسته می باشند. |  | 01-2294-444091 | 1401/11/19 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: