## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-RT-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1804 |  |  | Transmital Date: 17-Jan-2023
Document Title: Electrical Network (Load Flow, Motor Starting & Short Circuit) Study Report |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1804 |  |  | Transmital Date: 17-Jan-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-RT-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Section 3.3, The project document: Following documents shall be added as reference document: -Overall single line diagram -MV single line diagram -LV single line diagram -Cable List |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | اعمال گردید. |  |  | Noted and Closed.
2 | According to letter NO. 7393 date 1400.04.20, all network (Including transmission line, well pads, etc.) shall be considered in network study. |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | اعمال گردید. |  |  | See below item 15.
3 | The configuration for maximum short circuit study shall be rechecked and modified. (The worst case scenario shall be considered in maximum short circuit study) |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | اعمال گردید. |  |  | See below item 16.
4 | Minimum short circuit calculation shall be done and the relevant result shall be added to this section for Relay setting purpose. |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | اعمال گردید. |  |  | See below item 17.
5 | The configuration for motor starting study shall be clarify. (Worst case and Emergency scenario is necessary). |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | برای حالت راه اندازی موتور یک حالت فقط وجود دارد که آن نیز بدترین حالت می باشد. لذا حالت راه اندازی اضطراری وجود ندارد. چراکه موتورها توان بالا بوده و بر روی فیدر 11 کیلوولت نصب شده اند. |  |  | See below item 18.
6 | Critical and marginal reports in motor starting study shall be checked and modified base on requirement. |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | اعمال گردید. |  |  | Noted and Closed.
7 | Network study shall be done base on latest revision of etap software (19.0.1) and shall be submitted again to checked reports in native file. |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | نرما فزار سازمانی این مشارکت شماره 12 بوده که تفاوتی با ویرایش 19 از نرم افزار ندارد. |  |  | See below item 19.
8 | Section 5.1&5.2, Normal and Worst case Configuration: Shall be rechecked and modified base on above mentioned comment in item 2. |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | اعمال گردید. |  |  | See below item 20.
9 | Section 6, Load Flow Analysis: Reference data to comparing load flow result shall be added for example voltage margin, overloading, etc. |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | خروجی نرم افزار به صورت کامل در پیوست این مدرک ارسال شده است. |  |  | See below item 21.
10 | Section 7, Short Circuit Analysis: Switchgear tag shall be added. Meanwhile separate row shall be added for LV/MV capacitor bank. |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | بر اساس نام گذاری باسبارهای Etap، خروجی درج شده است. |  |  | See below item 22.
11 | different case studies shall be defined for load flow and short circuit calculations |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | همانطور که در ویرایش های قبلی اشاره شده است، سناریوهای مربوطه لحاظ شده است. ضمن اینکه مطالعه اتصال کوتاه مینیم نیز در نظر گرفته شد. |  |  | Noted and Closed.
12 | for load flow study summary tables shall be added to the document: - bus voltage summary table - transformers loading summary - Generators loading summary |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | خروجی خلاصه شده نرم افزار در انتهای فایلهای پیوست هر کدام از سناریوها وجود دارد. |  |  | See below item 23.
13 | for short circuit study summary tables shall be added to the document: - summary of maximum SC current per each case study - summary of minimum SC current for case that is applicable |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 |  |  |  | See below item 24.
14 | Complementary comments will be submitted after revised document. |  | BK-SUR-ENG-ELE-01-06832 | 2022-06-22 | در صورت وجود کامنتهای دیگر این مدرک ویرایش خواهد شد. |  |  | Noted and Closed.
15 | See above item 2: According to our telephone conversation, Not acceptable. Base on letter NO. 7393 date 1400.04.20, the load consumption has been considered wrong for example for Gureh and Binak (33KV), has been considered 1000KVA and 250KVA!!! And 1000KVA for binak desalting plant. Meanwhile the relevant transformer for above mentioned item shall be deleted. Meanwhile 1500KVA for cluster shall be added. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
16 | See above item 3: According to our telephone conversation it shall be rechecked and modified. (All bus shall be considered in calculation meanwhile the configuration shall be modified). |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
17 | See above item 4: According to our telephone conversation it shall be rechecked and modified. (All bus shall be considered in calculation). |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
18 | See above item 5: Worst case for MV motor starting is when the one of 25MVA power transformer is out of secrvice. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
19 | See above item 7: According to our telephone conversation, not acceptable. Base on scope of work, the network study shall be done base on latest revision of Etap software and native file shall be submitted to checked result reports. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
20 | See above item 8: Worst case study shall be shown base on wors scenario that is only One 25MVA, One 2000KVA and and 1000KVA is in service. Meanwhile diesel generator and related circuit breaker shall be shown. Meanwhile the number of ocupler in emergency configuration shall be modified. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
21 | See above item 9: According to our telephone conversation, not acceptable. A brief table of with considering voltage margin, overloading, etc. to comparsing load flow results shall be considered in document. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
22 | See above item 10: According to our telephone conversation, not acceptable. Switchgear tag shall be added base on relevant single line diagram to checked new technical characteristics of facilities such as new LV switchgear, etc. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
23 | See above item 12: According to our telephone conversation, not acceptable. A brief table of with considering voltage margin, overloading, etc. to comparsing load flow results (For bus voltage, transformer and generator loading) shall be considered in document. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
24 | See above item 13: According to our telephone conversation. Not acceptable. A brief table of with considering minimum SC currentshall be considered in document. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: