## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-MR-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2322 |  |  | Transmital Date: 8/29/2023
Document Title: PMR For Instrument/Plant Air & Nitrogen Packages |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-2322 |  |  | Transmital Date: 8/29/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-MR-0006_D03 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در متن صفحه 7 مدرک تغییر جزئی زیر اعمال گردد. |  | 1402-2294-264894 | 1402/07/08 | نقطه نظر کارفرمای محترم اعمال گردیده است
PLC based UCPs (one for each compressor) shall be considered to be mounted in control room and each of them had ability as selective master logic controller of complete air package (VTA). UCPs shall be connected to the PCS, ESD, for required monitoring, control functions and shutdowns as per P&ID. UCP panel door mounted HMI shall including alarm, trip and interlock logic annunciator lamp and buzzer (if any). LCP for local command is required for each compressor. SIL rated loops for safety and trip commands shall be considered. Lap top for engineering and maintenance and all original software and licences shall be prepared by vendor
2 | در متن صفحه 9 مدرک تغییر جزئی زیر اعمال گردد. |  | 1402-2294-264894 | 1402/07/08 | نقطه نظر کارفرمای محترم اعمال گردیده است
Package running status /common alarms/faults to be transferred to DCS via Air compressor UCP. Standalone control panel ( as minimum microprocessor based) located on each dryer skid for all required signaling, local logic, monitoring and etc. which shall be connected to control room mounted UCP of air compressor. Selective Master UCP of package shall allow each dryer to be worked as duty independent of compressor duty/standby selection.
3 | موارد فوق در مدارک پیوست مرتبط ( نقشه های P&ID و SPEC و ...) لحاظ شود و اصلاحات لازم انجام گردد. |  | 1402-2294-264894 | 1402/07/08 | نقطه نظر کارفرمای محترم در مدارک پیوست مرتبط لحاظ خواهد شد.
4 | ساختار کلی مدرک مورد تایید بوده و لیکن ارسال نسخه بعدی منوط به نهایی سازی مدارک مرتبطه مهندسی و درج نسخ تایید شده (AFC) است. معذالک جهت پرهیز از مکاتبات مضاعف و تسریع در تایید مدارک فوق، نهایی سازی مدارک پیش نیاز ( که در پیوست 1 مدرک اشاره شده است) در دستور کار تیم مهندس آن پیمانکار قرار گیرد. لذا مجدداً تاکید می گردد تا زمان نهایی شدن مدارک پیشنیاز، از ارسال ویرایش جدید مدرک پرهیز گردد. |  | 1402-2294-264894 | 1402/07/08 | مدرک MR پکیج هوا و نیتروژن به همراه آخرین ویرایش مدارک مرجع (ATTACHMENT#1) خدمت کارفرمای محترم ارسال می گردد.با توجه به اینکه مدارک پیوست تقریباً نهایی شده است لذا خواهشمند است جهت تسریع در امور خرید بررسی مدرک مذکور در دستور کار آن کارفرمای محترم قرار گیرد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: