## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1996 |  |  | Transmital Date: 05-Apr-2023
Document Title: Area Lighting & Small Power Layout |  |  |  |  | PEDCO Tr. No.: BBK-PEDCO-NISOC-0005-EL-TR-1996 |  |  | Transmital Date: 05-Apr-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-PY-0003_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as IFA after finalizing or minor comments on following documents: -Calculation Note For Outdoor Area Lighting System -Plot plan Drawing -Hazardous area classification layout |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید. |  |  | Noted and Closed.
2 | According to basic electrical design criteria, outdoor area lighting cables shall be 5 cores instead of 4 cores. So it shall be rechecked and modifid. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید. |  |  | Noted and Closed.
3 | Tower/Flood Lighting fixture/JB technical description shall be added to legend.( Lighting fixturers outdoor installation shall be considered IP65.) |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید. |  |  | Noted and Closed. (Note: IP65 shall be added to all outoor flourescent lighting fixturers (Bracket/Pole Mounted).)
4 | According to lighting towers locations, it seems, it is necessary to consider lighting fixturers for following locations in order to facilitate maintenance and repair activities during operation stage. : 1) Air coolers specially under air coolers 2) Flare KO. drum/Close drain and sump pumps and related walk way and stair way 3) Suction drums platform and stair ways 4) slug pums shelter and other paltform, walk way and stair way in project (If required.) |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید. |  |  | See below item 10.
5 | Typical installation detail for each lighting equipment shall be added and specified base on "Typical Installation Details & Notes For Lighting System". |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید. |  |  | Noted and Closed.
6 | If it is necessary to consider duct bank to pass the cable through the roads, it shall be shown. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید. |  |  | Noted and Closed. (Note: Duct bank for feeder No. NDP-01/F2 and socket feeders in utility area shall be added.)
7 | Emergency lighting shall be considered and shown in layout. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید. |  |  | Noted and Closed.
8 | Hazardous area classification layout shall be added as reference documents. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید. |  |  | Noted and Closed.
9 | Complementary comments will be submitted after received revised document. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | در صورت وجود هر گونه کامنت، متعاقبا اعمال خواهد شد. |  |  | Noted and Closed.
10 | See above item 4: Lighting fixtures for slug pumps sun shade has not been shown. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید.
11 | This document shall be revised after finalizing or minor comments base on NISOC/PEDCO comments on "Calculation Note For Outdoor Area Lighting System" document. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | این مدرک به همراه مدرک محاسباتی ارسال خواهد شد.
12 | Base on comments on "Calculation Note For Outdoor Area Lighting System" document, the lighting for roads in utility area shall be considered. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | با توجه به اینکه در محوطه موجود نیز چراغ روشنایی خیابانی وجود ندارد، در نتیجه محاسبات به گونه ای است که تمام سایت روشن خواهد شد.
13 | Latest revision of GCS plot plan shall be used for this document. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید.
14 | "Exd IIB T3" shall be added for all outdoor EX fluorescent lighting fixtures (Bracket/Pole Mounted). |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | به صورت نوت اضافه گردید.
15 | for elevated structures, lighting factures shall be shown on structure drawings. Also plan view and side view for structures and access platforms shall be added to this document in order to making sure all access platforms have adequate lighting fixtures. |  | BK-SUR-ENG-CIV-02-07381 | 2023-04-11 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: