## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  |  | BK |  | PPL | PEDCO | 320 |  | IN | DT | 0005 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  |  | OCT. 2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  |  | OCT. 2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  |  | MAY. 2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | MAR. 2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: |  |  | F9Z-708584
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | DT | 0005 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X |  |  | X |  |  |  | 67
4 | X | X |  |  | X |  |  |  | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN |  | DT | 0005 | D03
REFERENCE DOCUMENTS :
|  | Instrument & Control System Design Criteria | [5 empty] | BK-PPL-PEDCO-320-IN-DC-0001
|  | P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0001
|  | P&ID - Condensate Pipeline (to Binak PU) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0002
|  | Piping Material Specification | [5 empty] | BK-PPL-PEDCO-320-PI-SP-0001
|  | Pipeline Material Specification | [5 empty] | BK-PPL-PEDCO-320-PL-SP-0001
|  | Specification For Instrumentation | [5 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Specification For Pressure Safety Valves(PSV) | [5 empty] | BK-GNRAL-PEDCO-000-IN-SP-0007
|  | Instrument Hook-Up Diagram | [5 empty] | BK-PPL-PEDCO-320-IN-DG-0002
|  | Specification For Hazardous Area Classification | [5 empty] | BK-GNRAL-PEDCO-000-SA-SP-0002
D03

## Notes
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  | BK | PPL | PEDCO | 320 | IN | DT | 0005 | D03
GENERAL NOTES:
1- The pressure relief valves and its accessories shall be supplied pre-assembled. Valves shall be supplied as a whole, complete with all the accessories like cap, lifting lever, test gag, etc. All threaded and flanged openings shall be suitably covered to prevent entry of foreign material.
2- Effective discharge coefficient of pressure relief valves shall be 0.975 for gas and vapor and 0.62 for liquid services as a maximum.
3- The valve size shall be based on size calculations for the worst of all cases that might cause the valve to blow. For flanged pressure relief valves the orifice letter designation and the corresponding relieving area indicated in the EPC Contractor's data sheet will be as per API-526.
4- For a valve of given inlet and outlet sizes and letter designation, relieving area of the valves offered by Vendor, shall meet those in API-526 as a minimum.
5- The set pressure, over pressure and relieving pressure of the PSV depending upon maximum allowable working pressure and accumulation as per API Standard 520 Part I, and ASME Section VIII Division I or ASME Section I as the case may be.
6- If the set pressure is less than maximum allowable working pressure (MAWP), the overpressure could be more than accumulation. However, if PSV set pressure is same as MAWP, the accumulation and overpressure cannot exceed the accumulation. The relieving pressure would be set pressure plus overpressure.
7- ASME SECTION VIII DIV 1 stated a 10 % allowable over pressure over set pressure to achieve full lift of a single relief valve for blocked case. If the set pressure as maximum allowable working pressure (MAWP) set, the accumulation and over pressure is same and it is 10% over MAWP.
8- Emission shall be less than 85 dBA at 1 m distance from the valve.
9- For flanged valves, inlet and outlet sizes and ratings and center to flange face dimensions shall be in accordance with API-526. Dimensional tolerances shall be as mentioned there. If the design of pressure relief valve is such that liquid can collect on the discharge side of the disk, the valve shall be equipped with a drain at the lowest point where liquid can collect.
10- Valves shall, in general, be of the direct spring loaded full nozzle with minimum inlet flange rating of 300#, unless otherwise specified.
11- Nozzles of the forged type are preferable.
12- All valves shall be provided with a cap over the adjusting bolt.
13- Valve spring design shall not permit an adjustment of more than 5% above or 5% below that for which the valve is marked; unless the setting is within the spring design range established by the manufacturer or is determined to be acceptable to the manufacturer. The allowable tolerances in set pressures are as below: - ±0.14 bar for set pressures up to and including 4.8 barg. - ±3% for set pressures above 4.8 barg.
14- Materials of construction shall be suitable for the environmental conditions and the process conditions identified in the relevant instrument datasheets. Provision of corrosion resistant materials shall be considered for conventional valves for corrosive fluid. Materials to be used shall be in accordance with project piping material specification and relevant datasheets
15. In general, unless specifically identified otherwise in this specification and attachments, process wetted materials which are in contact with Corrosive Services (H2S, CO2, H2O), shall comply with the requirements of .. NACE MR0175/ISO 15156 . Body material shall normally be carbon steel and generally adhered to and consistent with project document “Piping Material Specification”.
16. According to "Specification For Pressure Safety Valves(PSV)", Valve bonnet or spring housing material shall be the same as the valve body material
17-According to "Process Basic of Design" Document, Environmental Condition For Field Instrumentation of BINAK Complex Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C)
Minimum ambient temperature: 5 (°C)
Maximum steel surface exposed to sun: 85 (°C)
Maximum summer dry bulb: 50 (°C)
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
18- Refer To Specification For Painting Doc.No.BK-GNRAL-PEDCO- 000-PI-SP-0006 Safety Valve Color Is not Specified So, Red Color Is Requested Considering Safety Factors , It Shall Be Finalized During KOM.
19- For Flammable Or Toxic Services, Bonnets Shall Be Vented To The Discharge Side Of The Relief Valve( In Conventional Type PSVs,).
20- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-3201
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  | BK | PPL |  | PEDCO | 320 | IN | DT |  | 0005 | D03
Item |  | Data Category | Technical Features | [7 empty] | Project Data & Requirements
1 |  | GENERAL | Tag Number | [7 empty] | PSV-3201
2 |  |  | P&ID NO and Page : | [7 empty] | BK-PPL-PEDCO-320- PR-PI-0001 _D04 (1 of 3)
3 |  |  | Service | [7 empty] | Pig Launcher
4 |  |  | Inlet Line No. |  |  | Outlet Line No. |  |  |  |  | GAS-113-0003-FN05-2"-PT |  |  |  | FL-113-0002-AN07-2"-PT
|  |  | Corrosion allowance inlet line |  |  | Outlet lkine |  |  |  |  | 3 mm |  |  |  | 6 mm
5 |  |  | Discharge to | [7 empty] | To LP Flare Header
6 |  |  | Protect Equipment | [7 empty] | Launcher
7 |  |  | Area Clacification for Discharge | [7 empty] | Zone 2, IIB T4
8 |  |  | Sour Service | [7 empty] | Yes
9 |  |  | NACE MR0175/ISO 15156 Compliance | [7 empty] | Yes
10 |  | BASIS | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
11 |  |  | Design Type |  |  | Safety, Relief, Safety-Relief |  |  |  |  | Saftey
12 | [5 empty] | Conventional, Bellow, Pilot Op. |  |  |  |  | Conventional
13 |  |  | Bonnet Type | [7 empty] | Closed
14 |  | PROCESS CONDITIONS (note 2) | Fluid / Phase / State | [7 empty] | Gas / 1-phase / Vapor
15 |  |  | Ambient Temperature °C | [7 empty] | 5-50 |  |  |  | 85
16 |  |  | Temperature °C |  |  | Operating |  |  |  |  | 58.3
17 |  |  | Pressure Barg |  |  | Operating |  |  |  |  | 50.9
18 |  |  | Oper. Temperature °C |  |  | RelievingTemp. °C |  |  |  |  | 58.30 |  |  |  | 212
19 |  |  | Required Capacity kg/h | [7 empty] | 1799.993
20 |  |  | Molecular Mass |  |  | Sp. Gr.@ relief Tmp kg/m3 |  |  |  |  | 24.58 |  |  |  | 0.84
21 |  |  | Oper. Pressure barg |  |  | Set Pressure barg |  |  |  |  | 50.9 |  |  |  | 62
22 |  |  | Back Pressure Barg |  |  | Constant |  |  |  |  | 0.5
23 | [5 empty] | Variable |  |  |  |  | 0
24 | [5 empty] | Total |  |  |  |  | 0.5
25 |  |  | % Allowable Overpressure | [7 empty] | 21%
26 |  |  | Over Pressure Factor | [7 empty] | 1.21
27 |  |  | Compressibility Factor (Z) | [7 empty] | 0.82
28 |  |  | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 1453
29 |  |  | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.448
30 |  |  | Density @ Oper. kg/m3 temprature & pressure | [7 empty] | 55.82
31 |  |  | Operating Viscosity cP | [7 empty] | 0.014
32 |  |  | Barometric Pressure (psia) | [7 empty] | 14.37
33 |  | SELECTION | Design Code |  |  | Sizing Basis |  |  |  |  | API 520 |  |  |  | -
34 |  |  | pressure relieving and de-pressurising systems Code | [7 empty] | API 521
35 |  |  | Design of Construction | [7 empty] | API 521
36 |  |  | Scenarios | [7 empty] | fire
37 |  |  | Basis of Selection | [7 empty] | fire
38 |  |  | Calculated Area cm² | [7 empty] | 0.359
39 |  |  | Selected Area cm² | [7 empty] | 1.539
40 |  |  | Accumulation AC % | [7 empty] | 121
41 |  |  | Orifice Designation | [7 empty] | D
42 |  | CONNECTIONS | Size: Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
43 |  |  | Rating & Facing : Inlet |  |  | Outlet |  |  |  |  | #600 RF |  |  |  | #150 RF
44 |  | MATERIALS (VTC) | Body and Bonnet | [7 empty] | A216 Gr. WCB (Note 15)
45 |  |  | Seat and Disc (Trim) | [7 empty] | SS316+RPTFE (Note 15)
46 |  |  | Nozzle | [7 empty] | SS 316 (Note 15)
47 |  |  | Guide and Rings | [7 empty] | SS 316 (Note 15)
48 |  |  | Spring | [7 empty] | A216 Gr. WCB (Note 16&20)
49 |  |  | Bellows | [7 empty] | N/A
50 |  | OPTIONS | Cap without Lever: Screwed or Bolted | [7 empty] | Screwed cap
51 |  |  | Lifting Lever: Plain or Packed | [7 empty] | N/A
52 |  |  | Test Gage | [7 empty] | Yes
53 |  |  | With Rupture Disc | [7 empty] | No
54 |  |  | Flame Arrestor | [7 empty] | No
55 |  |  | Hydro Test | [7 empty] | Required
56 |  |  | Seat Leakage Test | [7 empty] | Required
57 |  |  | Compliance Standard | [7 empty] | According to NACE MR-0175 / ISO15156
58 |  | PURCHASE | Manufacturer | [7 empty] | will be finalized later
59 |  |  | Model | [7 empty] | will be finalized later
60 |  |  | Serial No. | [7 empty] | will be finalized later
Main Notes:
VTA : Vendor to Advise in bidding stage VTC : Vendor to confirm in bidding stage N/A: Not applicable
D03

## PSV-3202
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  |  | BK | PPL |  | PEDCO | 320 | IN | DT |  | 0005 | D03
Item |  | Data Category | Technical Features | [7 empty] | Project Data & Requirements
1 |  | GENERAL | Tag Number | [7 empty] | PSV-3202
2 |  |  | P&ID NO and Page : | [7 empty] | BK-PPL-PEDCO-320- PR-PI-0001 _D04 (3 of 3)
3 |  |  | Service | [7 empty] | Pig Receiver
4 |  |  | Inlet Line No. |  |  | Outlet Line No. |  |  |  |  | GAS-113-0014-FN05-2"-PT |  |  |  | FL-113-0004-AN07-2"-PT
5 |  |  | Corrosion allowance inlet line |  |  | Outlet lkine |  |  |  |  | 3 mm |  |  |  | 6 mm
6 |  |  | Discharge to | [7 empty] | To Existing Flare System
7 |  |  | Protect Equipment | [7 empty] | Receiver
8 |  |  | Area Clacification for Discharge | [7 empty] | Zone 2, IIB T4
9 |  |  | Sour Service | [7 empty] | Yes
10 |  |  | NACE MR0175/ISO 15156 Compliance | [7 empty] | Yes
11 |  | BASIS | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
12 |  |  | Design Type |  |  | Safety, Relief, Safety-Relief |  |  |  |  | Relief
13 | [5 empty] | Conventional, Bellow, Pilot Op. |  |  |  |  | Conventional
14 |  |  | Bonnet Type | [7 empty] | Closed
15 |  | PROCESS CONDITIONS (note 2) | Fluid / Phase / State | [7 empty] | Gas / 1-phase / Vapor
16 |  |  | Ambient Temperature °C | [7 empty] | 5-50 |  |  |  | 85
17 |  |  | Temperature °C |  |  | Operating |  |  |  |  | 31.3
18 |  |  | Pressure Barg |  |  | Operating |  |  |  |  | 40
19 |  |  | Oper. Temperature °C |  |  | RelievingTemp. °C |  |  |  |  | 31.30 |  |  |  | 289
20 |  |  | Required Capacity kg/h | [7 empty] | 4300.75
21 |  |  | Molecular Mass |  |  | Sp. Gr.@ relief Tmp kg/m3 |  |  |  |  | 24.58 |  |  |  | 0.84
22 |  |  | Oper. Pressure barg |  |  | Set Pressure barg |  |  |  |  | 40 |  |  |  | 62
23 |  |  | Back Pressure Barg |  |  | Constant |  |  |  |  | 0.5
24 | [5 empty] | Variable |  |  |  |  | 0
25 | [5 empty] | Total |  |  |  |  | 0.5
26 |  |  | % Allowable Overpressure | [7 empty] | 21%
27 |  |  | Over Pressure Factor | [7 empty] | 1.21
28 |  |  | Compressibility Factor (Z) | [7 empty] | 0.827
29 |  |  | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 1453
30 |  |  | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.437
31 |  |  | Density @ Oper. kg/m3 temprature & pressure | [7 empty] | 49.09
32 |  |  | Operating Viscosity cP | [7 empty] | 0.01
33 |  |  | Barometric Pressure (psia) | [7 empty] | 14.37
34 |  | SELECTION | Design Code |  |  | Sizing Basis |  |  |  |  | API 520 |  |  |  | -
35 |  |  | pressure relieving and de-pressurising systems Code | [7 empty] | API 521
36 |  |  | Design of Construction | [7 empty] | API 521
37 |  |  | Scenarios | [7 empty] | fire
38 |  |  | Basis of Selection | [7 empty] | fire
39 |  |  | Calculated Area cm² | [7 empty] | 0.938
40 |  |  | Selected Area cm² | [7 empty] | 1.539
41 |  |  | Accumulation AC % | [7 empty] | 121
42 |  |  | Orifice Designation | [7 empty] | E
43 |  | CONNECTIONS | Size: Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
44 |  |  | Rating & Facing : Inlet |  |  | Outlet |  |  |  |  | #600 RF |  |  |  | #150 RF
45 |  | MATERIALS (VTC) | Body and Bonnet | [7 empty] | A216 Gr. WCB (Note 15)
46 |  |  | Seat and Disc (Trim) | [7 empty] | SS316+RPTFE (Note 15)
47 |  |  | Nozzle | [7 empty] | SS 316 (Note 15)
48 |  |  | Guide and Rings | [7 empty] | SS 316 (Note 15)
49 |  |  | Spring | [7 empty] | A216 Gr. WCB (Note 16&20)
50 |  |  | Bellows | [7 empty] | N/A
51 |  | OPTIONS | Cap without Lever: Screwed or Bolted | [7 empty] | Screwed cap
52 |  |  | Lifting Lever: Plain or Packed | [7 empty] | N/A
53 |  |  | Test Gage | [7 empty] | Yes
54 |  |  | With Rupture Disc | [7 empty] | No
55 |  |  | Flame Arrestor | [7 empty] | No
56 |  |  | Hydro Test | [7 empty] | Required
57 |  |  | Seat Leakage Test | [7 empty] | Required
58 |  |  | Compliance Standard | [7 empty] | According to NACE MR-0175 / ISO15156
59 |  | PURCHASE | Manufacturer | [7 empty] | will be finalized later
60 |  |  | Model | [7 empty] | will be finalized later
61 |  |  | Serial No. | [7 empty] | will be finalized later
Main Notes:
VTA : Vendor to Advise in bidding stage VTC : Vendor to confirm in bidding stage N/A: Not applicable
D03