## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LEVEL GAUGES
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0003 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR LEVEL GAUGES نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  |  | OCT.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  |  | MAY.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: 'F9Z-708924
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LEVEL GAUGES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0003 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | X | [5 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LEVEL GAUGES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0003 | D03
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## Notes
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LEVEL GAUGES
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0003 | D03
GENERAL NOTES:
1 - Materials indicated in the data sheets have to be intended as a guide. Vendor is responsible for the selection of materials suitable for the specified working conditions.
2 - Material Test Certificate and calibration Certificate for all gauges to be submitted by Vendor.
3 - Tag plate as per Specification for Instrumentation, shall be stainless steel 304 SS (VTC). Following details shall be engraved on them:
• Tag Number • Range Limit • Service • Manufacture Model
4 - Environmental condition for field instrumentation of Binak oilfield shall be considered as per the following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design"):
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
5- Gauge cock valve shall be quick closing and lever operated.
6- Each sectionof Level gauges shall have a visible length of approximately 300mm.

## LG
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LEVEL GAUGES
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT |  | 0003 | D03
LEVEL GAUGE
| GENERAL DATA |  | 1 | Tag No. | [6 empty] | SEE PAGE 6
|  |  | 2 | P& ID | [6 empty] | SEE PAGE 6
|  |  | 3 | Euipment No. | [6 empty] | SEE PAGE 6
|  |  | 4 | Area Clacification | [6 empty] | Zone 2, IIA T3 (Note 2)
5
| PROCESS CONDITION |  | 6 | Upper Fluid |  |  | Lower Fluid |  |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 7 | Ope. Temp. |  |  | Des. Temp. |  | (°C) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 8 | Ope. Press. |  |  | Des. Press. |  | (barg) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 9 | Upper Density |  |  | Lower Density |  | (kg/m3) |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  |  | 10 | Visible Length |  |  |  |  | (mm) |  | SEE PAGE 6
| GAUGE |  | 11 | Type |  |  | Gauge Glass Type |  |  |  | SEE PAGE 6 |  |  | Heat resistant borosilicate glass
|  |  | 12 | Centre - Centre | [6 empty] | SEE PAGE 6
|  |  | 13 | Size/Section | [6 empty] | SEE PAGE 6
|  |  | 14 | Rating (lbs)/Finish Flange | [6 empty] | SEE PAGE 6
|  |  | 15 | Vessel Connection | [6 empty] | SEE PAGE 6
|  |  | 16 | Process Connection (Note 1) | [6 empty] | 2" Flanged
|  |  | 17 | Body Material | [6 empty] | CS-A216 GR WCB
|  |  | 18 | Connection Arrangement | [6 empty] | Side-Side
|  |  | 19 | Float Type | [6 empty] | N/A
|  |  | 20 | Float Material | [6 empty] | N/A
|  |  | 21 | Illuminator | [6 empty] | N/A
|  |  | 22 | Power Supply | [6 empty] | N/A
|  |  | 23 | Electrical Connection | [6 empty] | N/A
|  |  | 24 | Electrical Certification | [6 empty] | N/A
|  |  | 25 | Cable Type | [6 empty] | N/A
|  |  | 26 | Ingress Protection | [6 empty] | IP-65as minimum
| GAUGE COCK |  | 27 | Type | [6 empty] | Ball valve
|  |  | 28 | Body Material |  |  | Trim Material |  |  |  | Forged Carbon Steel |  |  | 316 S.S
|  |  | 29 | Seat |  |  | Safety Ball |  |  |  | Double Seat |  |  | Required
|  |  | 30 | Gauge Conn. | [6 empty] | VTA
|  |  | 31 | Bonnet | [6 empty] | Screwed
|  |  | 32 | Ball Check | [6 empty] | Required
|  |  | 33 | Renewable Seat | [6 empty] | No
|  |  | 34 | Construction | [6 empty] | VTA
| OPTIONS |  | 35 | Drain Valve |  |  | Drain Conn. |  |  |  | Required |  |  | 3/4 "
|  |  | 36 | Vent Valve |  |  | Vent Conn. |  |  |  | Required |  |  | 3/4 "
|  |  | 37 | X Ray Inspection | [6 empty] | No
|  |  | 38 | NACE Requirements | [6 empty] | SEE PAGE 6
| PURCHASING DATA |  | 39 | Model | [6 empty] | Will be finalized later
|  |  | 40 | Supplier | [6 empty] | Will be finalized later
NOTES:
VTA : Vendor To Advise
1- Refer to Typical Hookup Drawing for Detail of Installation Doc No. "BK-GCS-PEDCO-120-IN-DG-0002"
2- All Level Gauges to be considered for not transparent fluid.

## LG LIST
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LEVEL GAUGES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 | [5 empty] | BK |  | GCS | PEDCO | 120 |  | IN |  | DT |  | 0003 |  | D03
Rev. | Item No. | Tag No. | P&ID No. | Equipment No. | Service |  | Viscosity | Fluid |  | Phase |  | Design Pressure (barg) | Operating Pressure (barg) | Design Temp. (°C) | Operating Temp. (°C) | Density (kg/m3) |  | Visible Length (mm) | Type (Note 2) | C-C (mm) | Section × Size Type of glasses | Qty. of connection | Size | Flange Rating/ Finish | Illuminator | Nace | Remark
[8 empty] | Upper | Lower | Upper | Lower |  |  |  |  | Upper | Lower
D03 Modified | 1 | LG-2111A | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) (Rev.07) | V-2104 | SLUG CATCHER DRUM |  | 0.76644 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/9 | 5.5 | 85 | 32 | 6.2141 | 845.5455 | 1400 | REFLEX | 1650(VTC) | 4×9 | 2 | 2" | 300#/RF | NO | YES | LG-2111 Part 1
D03 Modified | 2 | LG-2111B | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) (Rev.07) | V-2104 | SLUG CATCHER DRUM |  | 0.76644 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/9 | 5.5 | 85 | 32 | 6.2141 | 845.5455 | 1400 | REFLEX | 1650VTC) | 4×9 | 2 | 2" | 300#/RF | NO | YES | LG-2111 Part 2
D03 Modified | 2 | LG-2111C | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) (Rev.07) | V-2104 | SLUG CATCHER DRUM |  | 0.76644 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/9 | 5.5 | 85 | 32 | 6.2141 | 845.5455 | 1400 | REFLEX | 1650(VTC) | 4×9 | 2 | 2" | 300#/RF | NO | YES | LG-2111 Part 3
D03 Modified | 6 | LG-2116 | BK-GCS-PEDCO-120-PR-PI-0005 (Rev.07) | V-2105 | INLET KNOCK OUT DRUM |  | 0.69 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/9 | 5.3 | 85 | 37.17 | 6.1649 | 842.581 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 300#/RF | NO | YES
D03 Modified | 7 | LG-2121A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) (Rev.07) | V-2101-A | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #A |  | 0.69 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/9 | 5.1 | 85 | 36.92 | 5.9689 | 842.661 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 300#/RF | NO | YES
D03 Modified | 8 | LG-2121B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) (Rev.07) | V-2101-B | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #B |  | 0.69 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/9 | 5.1 | 85 | 36.92 | 5.9689 | 842.661 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 300#/RF | NO | YES
D03 Modified | 9 | LG-2121C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) (Rev.07) | V-2101-C | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #C |  | 0.69 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/9 | 5.1 | 85 | 36.92 | 5.9689 | 842.661 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 300#/RF | NO | YES
D03 Modified | 10 | LG-2131A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) (Rev.07) | V-2102-A | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #A |  | 0.44 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/22 | 18.3 | 115.4 | 60 | 18.3 | 829.0943 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 300#/RF | NO | YES
D03 Modified | 11 | LG-2131B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) (Rev.07) | V-2102-B | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #B |  | 0.44 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/22 | 18.3 | 115.4 | 60 | 18.3 | 829.0943 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 300#/RF | NO | YES
D03 Modified | 12 | LG-2131C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) (Rev.07) | V-2102-C | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #C |  | 0.44 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/22 | 18.3 | 115.4 | 60 | 18.3 | 829.0943 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 300#/RF | NO | YES
D03 Modified | 13 | LG-2141 | BK-GCS-PEDCO-120-PR-PI-0012 (Rev.07) | V-2103 | GAS COMPRESSION DISCHARGE DRUM |  | 0.49 | PROCESS GAS | HYDROCARBON DRAIN | G | L | F.V/62 | 54.1 | 130 | 60 | 59.6331 | 982.0159 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 600#/RF | NO | YES
D03 | 14 | LG-2162A | BK-GCS-PEDCO-120-PR-PI-0014 (Rev.07) | TK-2102 | LEAN GLYCOL STORAGE TANK |  | 6.63 | NITROGEN GAS | TRIETHYLENE GLYCOL | G | L | FULL OF WATER+ 160MBARG/-7MBARG | 0.1 | 85 | AMB | 1.035 | 1100-1135 | 1400 | REFLEX | 1650 (VTC) | 4× 9 | 2 | 2" | 300#/RF | NO | NO | LG-2162 Part 1
D03 | 15 | LG-2162B | BK-GCS-PEDCO-120-PR-PI-0014 (Rev.07) | TK-2102 | LEAN GLYCOL STORAGE TANK |  | 6.63 | NITROGEN GAS | TRIETHYLENE GLYCOL | G | L | FULL OF WATER+ 160MBARG/-7MBARG | 0.1 | 85 | AMB | 1.035 | 1100-1135 | 1400 | REFLEX | 1650 (VTC) | 4× 9 | 2 | 2" | 300#/RF | NO | NO | LG-2162 Part 2
D03 | 16 | LG-2162C | BK-GCS-PEDCO-120-PR-PI-0014 (Rev.07) | TK-2102 | LEAN GLYCOL STORAGE TANK |  | 6.63 | NITROGEN GAS | TRIETHYLENE GLYCOL | G | L | FULL OF WATER+ 160MBARG/-7MBARG | 0.1 | 85 | AMB | 1.035 | 1100-1135 | 1400 | REFLEX | 1650 (VTC) | 4× 9 | 2 | 2" | 300#/RF | NO | NO | LG-2162 Part 3
D03 Modified | 17 | LG-2201 | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) (Rev.07) | V-2203 | INSTRUMENT AIR RECEIVER |  | 0.49 | INSTRUMENT AIR | WATER | G | L | 12.5 | 8 | 85 | 65 | 9.2785 | 976.7586 | 680 | REFLEX | 1000 (VTC) | 2× 9 | 2 | 2" | 300#/RF | NO | NO
D03 Modified | 18 | LG-2211 | BK-GCS-PEDCO-120-PR-PI-0016 (Rev.07) | V-2204 | NITROGEN RECEIVER |  | 0.49 | NITROGEN GAS | WATER | G | L | 12.5 | 8 | 85 | 60 | 9.1263 | 976.7586 | 680 | REFLEX | 1000 (VTC) | 2× 9 | 2 | 2" | 300#/RF | NO | NO
D03 Modified | 19 | LG-2221A | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) (Rev.07) | V-2202 | CLOSED DRAIN DRUM |  | 0.89 | FLARE GAS | HYDROCARBON DRAIN | G | L | F.V/6 | ATM | 85 | AMB | 5.19 | 978.6278 | 1400 | REFLEX | 1650 (VTC) | 4× 9 | 2 | 2" | 300#/RF | NO | YES | LG-2221 Part 1
D03 Modified | 20 | LG-2221B | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) (Rev.07) | V-2202 | CLOSED DRAIN DRUM |  | 0.89 | FLARE GAS | HYDROCARBON DRAIN | G | L | F.V/6 | ATM | 85 | AMB | 5.19 | 978.6278 | 1400 | REFLEX | 1650 (VTC) | 4× 9 | 2 | 2" | 300#/RF | NO | YES | LG-2221 Part 2
D03 Modified | 21 | LG-2251 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) (Rev.07) | V-2201 | LP FLARE K.O. DRUM |  | 0.46 | FLARE GAS | HYDROCARBON DRAIN | G | L | F.V/6 | 0.5 | 85 | 32 | 5.19 | 978.6278 | 680 | REFLEX | 950 (VTC) | 2× 9 | 2 | 2" | 300#/RF | NO | YES
D03 Modified | 22 | LG-2271 | BK-GCS-PEDCO-120-PR-PI-0022 (Rev.07) | V-2205 | FUEL GAS K.O. DRUM |  | 0.69 | FLARE GAS | HYDROCARBON DRAIN | G | L | F.V/9 | 4.9 | 85 | 48 | 5.7715 | 842.661 | 1040 | REFLEX | 1300 (VTC) | 3× 9 | 2 | 2" | 300#/RF | NO | YES
D03 | 23 | LG-2281 | BK-GCS-PEDCO-120-PR-PI-0023 (Rev.07) | V-2206A | DIESEL OIL DRUM |  | N.A. | DIESEL OIL | DIESEL OIL | G | L | ATM+FULL OF LIQUID | ATM | 85 | AMB | 1 | 850 | 1760 | REFLEX | 2000 (VTC) | 5× 9 | 2 | 2" | 300#/RF | NO | NO
(1) VTA: Vendor To Advise |  |  |  | VTC: Vendor To Confirm |  |  | G: Gas |  | L: Liquid
(2) Armored type level Gauge to be used.
D03

## Float and Cable LG List
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LEVEL GAUGES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0003 | D03
Datashet for Float and Cable Level Gauge
| 1 | Tag number |  |  |  | LG-2301 |  |  |  |  | LG-2302
| 2 | Quantity |  |  |  | 1 |  |  |  |  | 1
| 3 | P&ID number |  |  |  | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  |  |  |  | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2)
| 4 | Tag vessel / Class |  |  |  | TK-2301-A | 150# |  |  |  | TK-2301-B | 300 #
| 5 | NACE MR 0175 |  |  |  | No |  |  |  |  | No
| 6 | Manufacturer |  |  |  | VTA |  |  |  |  | VTA
| 7 | Series / Model no |  |  |  | VTA |  |  |  |  | VTA
| 8 | PROCESS DATA
| 9 | Fluid |  |  |  | Fire Water |  |  |  |  | Fire Water
| 11 | Design/Operating Pressure (Barg) |  |  |  | Full Of Water /ATM |  |  |  |  | 3.5 /2.3
| 12 | Design/Operating Temperature (°c) |  |  |  | 85° C/ AMB |  |  |  |  | 85° C/ AMB.
| 13 | Viscosity (cP) |  |  |  | 1.02 |  |  |  |  | 1.02
| 13 | Density (Kg/m3) |  |  |  | 1000 |  |  |  |  | 1000
| 14 | GENERAL FEATURES
| 15 | Type : |  |  |  | Float and Cable Level Gauge |  |  |  |  | Float and Cable Level Gauge
| 16 | Float Material |  |  |  | PVC |  |  |  |  | PVC
| 17 | Float Dimention |  |  |  | VTA |  |  |  |  | VTA
| 18 | Visible/Cable Length |  |  |  | 9500 mm/VTA |  |  |  |  | 9500 mm/VTA
| 19 | Cable Material |  |  |  | VTA |  |  |  |  | VTA
| 23 | Accuracy |  |  |  | 2%of Full Scale |  |  |  |  | 2%of Full Scale
| 24 | ISOLATION VALVES
| 25 | Angle valve offset type (integrally mounted) |  |  |  | N/A |  |  |  |  | N/A
| 26 | 1/4 turn operating |  |  |  | N/A |  |  |  |  | N/A
| 27 | Simple seat / Double seat |  |  |  | - | - |  |  |  | -
| 28 | Safety check ball |  |  |  | No |  |  |  |  | No
| 29 | Isolation Valve/ material |  |  |  | N/A | N/A |  |  |  | N/A | N/A
| 31 | CONNECTION PROCESS
| 32 | Flanges / Stand pipe mounting |  |  |  | Flanged, 6" | N/A |  |  |  | Flanged, 6" | N/A
| 33 | Rating / Flange finish |  |  |  | 300# | N/A |  |  |  | 300# | N/A
| 34 | Flange material |  |  |  | A-105 |  |  |  |  | A-105
| 35 | Stamped tag number |  |  |  | N/A |  |  |  |  | N/A
| 36 | Drain Connection/ Material |  |  |  | N/A |  |  |  |  | N/A
| 37 | Vent Connection / Material |  |  |  | N/A |  |  |  |  | N/A
| 38 | Connection orientation |  |  |  | Hanked type through cable and spool |  |  |  |  | Hanked type through cable and spool
| 39 | Cock Valve |  |  |  | N/A |  |  |  |  | N/A
| 40 | ACCESSORIES
| 41 | Access Plat Form |  |  |  | Yes |  |  |  |  | N/A
| 42 | Ingress Protection |  |  |  | IP 65 min |  |  |  |  | IP 65 min
| 43 | Cable and Spool |  |  |  | Yes |  |  |  |  | Yes
| 44 | Cable entry |  |  |  | - |  |  |  |  | -
| 45 | Cable gland |  |  |  | - |  |  |  |  | -
| 46 | Electrical Protection |  |  |  | - |  |  |  |  | -
General Notes :
1- All wetted part material shall be SS 316.
VTA : Vendor To Advise
2-Any Installation Accessories (Rod , Flange , Ruler ,….) To Be Provided By Vendor.