## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-ST-DW-0011_D00 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-T-2332 |  |  | Transmital Date:9/5/2023
Document Title: Structural Drawing For Switchgear Building For Well Pads - W007S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-ST-T-2332 |  |  | Transmital Date:9/5/2023
[5 empty] | CRS No:NISOC-CRS-BK-W007S-PEDCO-110-ST-DW-0010_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 |  |  | 1402-2294-260099 | 1402/07/04 | مطابق با بند 4-8-1 نشریه 038 (ویرایش سوم) ، برای سازه های با ارتفاع کمتر از 50 متر و نامنظمی در پلان نوع پ ، می توان ازروش بار جانبی معادل برای اعمال نیروی زلزله استفاده کرد و نیازی به بکارگیری روش دینامیکی نمی باشد . همچنین با توجه به جدول 4-2 نشریه 038 با درنظر گرفتن دیافراگم صلب در سقف و احراز شرط (max/∆ave∆) در ردیف الف ، سازه مذکور دارای نامنظمی پیچشی نمی باشد .
2 |  |  | 1402-2294-260099 | 1402/07/04 | کلیه ابعاد ، اندازه ها و کدهای ارتفاعی منطبق با آخرین مدرک معماری (AFC) می باشد .
3 |  |  | 1402-2294-260099 | 1402/07/04 | اعمال می گردد .
4 |  |  | 1402-2294-260099 | 1402/07/04 | مجددا ارسال می گردد .
5 |  |  | 1402-2294-260099 | 1402/07/04 | با توجه به استفاده از قاب خمشی ویژه و در نظر گرفتن ضوابط آرماتورگذاری قاب های ویژه ، مطابق با بند9-20-6-3-2-4 مبحث نهم مقررات ملی ، محل وصله ستون فقط در نیمه میانی طول ستون مجاز می باشد.
6 |  |  | 1402-2294-260099 | 1402/07/04 | کلیه ضوابط آرماتورگذاری مرتبط با قاب خمشی ویژه درکلیه قسمت های سازه رعایت شده است .
7 |  |  | 1402-2294-260099 | 1402/07/04 | درشیت شماره 3 تراز ارتفاعی کلیه تیرها و در شیت شماره 2 تراز ارتفاعی کلیه ستون ها ارائه شده است .
8 |  |  | 1402-2294-260099 | 1402/07/04 | همانطور که در بندهای دیگر عنوان گردید کلیه تراز ها ی ارتفاعی منطبق با مدرک معماری می باشند .
9 |  |  | 1402-2294-260099 | 1402/07/04 | اعمال می گردد .
10 |  |  | 1402-2294-260099 | 1402/07/04
Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Legend
| CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
Signature | Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: