## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-PY-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1468 |  |  | Transmital Date: 10/9/2022
Document Title: F&G Location Layout For Process Area |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1468 |  |  | Transmital Date: 10/9/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-PY-0005_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در AREA-3 در زیر سایه بان مواد شیمیای ، نیازی به نصب دتکتور گاز قابل اشتعال و سمی نمی باشد |  | 1401-2294-286131 | 1401/08/08 | درخواست کارفرمای محترم اعمال گردید
2 | در AREA-6 دتکتور FD-6002 بصورت قطری درون SUMP جابجا شود |  | 1401-2294-286131 | 1401/08/08 | درخواست کارفرمای محترم اعمال گردید
3 | در Area -8 دتکتور FD-8001 به زیر سایه بان دیزل ژنراتور جابجا شود |  | 1401-2294-286131 | 1401/08/08 | درخواست کارفرمای محترم اعمال گردید
4 | MAC-6001 به داخل Pit جابجا شود |  | 1401-2294-286131 | 1401/08/08 | درخواست کارفرمای محترم اعمال گردید
5 | لازم بذکر است یک آلارم دیداری و شنیداری و یک شستی اعلان حریق نزدیک درب خروجی سایت ( کنار حراست ) نصب شود |  | 1401-2294-286131 | 1401/08/08 | درخواست کارفرمای محترم اعمال گردید
6 | لازم بذکر است یک آلارم دیداری و شنیداری در بیرون ساختمان کنترل کنار درب ورودی اصلی اضافه گردد |  | 1401-2294-286131 | 1401/08/08 | در مدرک F&G LOCATION LAYOUT FOR BUIDING اضافه می شود
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: