## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-PY-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1459 |  |  | Transmital Date: 10/4/2022
Document Title: F&G Location Layout For Buildings |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1459 |  |  | Transmital Date: 10/4/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-PY-0006_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در ساختمان کنترل اتاق 111 ، دتکتور حرارتی جایگزین دتکتور دودیاب شود |  | 1401-2294-280846 | 1401/08/03 | با توجه به اینکه ساختمان کنترل موجود جایگزین ساختمان کنترل جدید شد لذا در اتاق مد نظر از ساختمان کنترل موجود یک عدد دتکتور حرارتی نصب می باشد.
2 | در ساختمان کنترل اتاق 114 نیازی به نصب دتکتور نمی باشد |  | 1401-2294-280846 | 1401/08/03 | با توجه به اینکه ساختمان کنترل موجود جایگزین ساختمان کنترل جدید شد دتکتوری در اتاق مدنظر نصب نمی گردد
3 | در ساختمان کنترل اتاق 115 دتکتور دودیاب نصب شود |  | 1401-2294-280846 | 1401/08/03 | با توجه به اینکه در طراحی جدید ساختمان کنترل موجود Extended شده است اتاق BOILER وجود ندارد
4 | در نقشه ساختمان کنترل ابعاد اضافه شود |  | 1401-2294-280846 | 1401/08/03 | اصلاح گردید
| در ساختمان برق ، MAC-1201 به بیرون ساختمان منتقل شود |  | 1401-2294-280846 | 1401/08/03 | اصلاح گردید
| در ساختمان MAC-1301 ، CCTV به بیرون از ساختمان کنترل منتقل شود |  | 1401-2294-280846 | 1401/08/03 | اصلاح گردید
| در ساختمان CCTV ، اتاق 103 نیازیبه نصب دتکتور نمی باشد |  | 1401-2294-280846 | 1401/08/03 | اصلاح گردید
| در ساختمان CCTV ، اتاق 102 دتکتور حرارتی جایگزین دتکتور دودیاب شود |  | 1401-2294-280846 | 1401/08/03 | اصلاح گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: