## Sheet1
| N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
| Document No: BK-GCS-PEDCO-120-ME-TB-0006_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1938 |  |  | Transmital Date: 06/MARCH/2023
| Document Title: TBE For Instrument/Plant Air & Nitrogen Packages |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-1938 |  |  | Transmital Date: 06/MARCH/2023
[6 empty] | CRS No: CRS-BK-GCS-PEDCO-120-ME-TB-0006_D00 |  |  | CRS Status:
|  | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Mechanical Comments :
Instrument & Plant Air Production Package :
| 1 | Section 2 : This section shall be in according to VDR from related MR. 2.9 : Special tools for erection and maintenance shall provided by vendor , for SAT test & pre-commissioning & commissionig shall be clarified. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 2.Vendor will be stamp and signe MR documents. 2.9 Noted,Sat test & pre commissioning & commissioning shall be in According to the project specification
| 2 | Section 3 : This section shall be in according to MR , for example Common baseplate for driver and compressor shall be added. 3.2 : Coupling type shall be dry flexible spacer whit Non sparking guard. 3.6 : in according to duty spec , Inlet filter shall be auto cleaning type. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 3.Vendor will be stamp and signe MR documents. 3.2 Noted 3.6 Noted
3 | 3 | Section 4 : This section shall be in according to MR,For example KOM and FINAL DATA BOOK shall be added. 4.11 : this item shall be in according to MR 4.14 : this item shall be accepted by all vendors |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 4.: TBE is according to MR,that Vendor will be stamp and signe MR documents.
| 4 | Section 5 : Site condition shall be comleted in according to desigh criteria. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 5.: 'Noted,All vendors have accepted
| 5 | 6.17 : This item shall be specified by all vendors. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 6.17: 'Noted, All vendors will update their technical offer after P.O
| 6 | 8.12 : This item shall be specified by all vendors. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 8.12: 'All vendors have accepted
Nitrogen Production Package :
| 1 | Section 2 : This section shall be in according to VDR from related MR. 2.9 : Special tools for erection and maintenance shall provided by vendor , for SAT rest & pre-commissioning & commissionig shall be clarified. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 2:.Vendor will be stamp and signe MR documents. 2.9: Noted,Sat test & pre commissioning & commissioning shall be in According to the project specification
| 2 | Section 3 : This section shall be in according to VDR from related MR and duty spec. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 3.: Vendor will be stamp and signe MR documents.
| 3 | Section 4 : This section shall be in according to MR,For example KOM and FINAL DATA BOOK shall be added. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 4.:TBE is according to MR,that Vendor will be stamp and signe MR documents.
| 4 | Section 5 : Site condition shall be comleted in according to desigh criteria. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 5.:'All vendors have accepted
| 5 | 6.15 : This item shall be specified by all vendors. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | 6.15: All vendors have accepted
Process comments :
| 1 | در خصوص شركت هوايار موارد زير اعلام مي گردد :‌ 1-ظرفیت کمپرسور هوا با مدرک Duty Spec مطابقت ندارد. 2- فشار طراحی سیستم پایین دست کمپرسور با عدد 12.5 بار نسبی درج شده در مدرک Duty Spec و مدرک P&ID، تطابق ندارد. 3- ظرفیت درج شده برای کمپرسور هوا در صفحه 4 با ظرفیت کمپرسور HF-55 در صفحه 8، تفاوت دارد. 4- میزان افت فشار برای خشک کن در دیتا شیت درج گردد.. 5- فشار طراحی تجهیزات پایین دست کمپرسور بسته نیتروژن، با عدد 12.5 بار مندرج در Duty Spec مغایرت دارد. 6- عدد نقطه شبنم -70 درجه در فشار اتمسفریک در داده برگ سازنده درج گردد. 7- برای کنترل میزان CO2 و CO در خروجی N2 PK ( مطابق موارد مندرج در Duty Spec) چه تمهیدی توسط سازنده در نظر گرفته شده است؟ |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | پیشنهاد فنی شرکت هوایار به همراه لیست انحرافات به روز رسانی گردیده و به پیوست TBE قرار داده شده است لذا خواهشمند است مدارک را مجددا بررسی فرمایید. همچنین در خصوص مغایرت ها مدارک بعد از P.O نهایی خواهد شد و توسط سازندگان محترم ارسال می گردد
Instrument comments :
Nitrogen Production Package :
| 1 | Please clarify about control board type for HAVAYAR(OR PANEL) |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | S7 400 H
| 2 | The location of N2 control panel to be clarify. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | UCP at control building LCP at build
| 3 | There is some Discrepancy about the quantity of N2 control panel between instrument documents (block diagram and HAVAYAR technical offer).This item to be clarify. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | all Vendors will update their technical offer with their documents after P.O
Instrument & Plant Air Production Package :
| 1 | For HAVAYAR : For air compressor PLC based panel to be specified |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | As per project specification, PLC based UCP (for control and safety) dedicated to each compressor is requested for both package (N2 and air): -One PLC based UCP for each compressor (totally 2.Nos. located on control room) for Air compressor package (type C). one of UCP shall be considered as master. -One PLC based UCP for nitrogen package (located on control room) (type C).
| 2 | For HAVAYAR : According to latest instrument comments on Duty spec. the artichecture of panel to be finalized based on client request. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | Noted
Genral comments :
| 1 | Spare part shall be in according to contract spare part list. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | Noted
| 2 | please find the attached file. |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | All vendors have accepted
| 3 | All Sub-Vendors shall be selected form AVL |  | BK-SUR-ENG-MEC-01-07241 | 2023-03-15 | All vendors have accepted
| Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
| Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
|  | Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: S.Zafaresmaeili | Signature | M.Fakharian
|  | Date: 3/15/2023 |  |  |  |  | Date: 10/24/2023