## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-AR-DW-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2290 |  |  | Transmital Date: 8/7/2023
Document Title:Architectural Drawing For Utility Shelter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-AR-TR-2290 |  |  | Transmital Date: 8/7/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-AR-DW_0005 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | تراز ارتفاعی روی پدستالها درج شود |  | 1402-2294-223974 | 1402/06/06 | اعمال گردید
2 | عنوان مدرک ارایه شده در شیت 1/7 با عنوان 120-CV-DW-0007 در لیست مدارک پروژه موجود نمیباشد اصلاح شود |  | 1402-2294-223974 | 1402/06/06 | به BK-GCS-PEDCO-120-CV-PY-0005 تغییریافت
3 | درشیت 6/7 برای ورق فلاشینگ به عبارت HOT DIP GALVANIZED FLASHING 0.7mm وجهت ورق گاتر HOT DIP GALVANIZED FLASHING 1mm اصلاح گردد. |  | 1402-2294-223974 | 1402/06/06 | اعمال گردید
4 | مقتضی است درمدرک سازه پلان کفسازی دریک شیت جداگانه بالحاظ کلیع درزهای حرکتی و همچنین درزها در محل اتصال کفسازی بتنی به سایر المانها/تجهیزات به همراه دیتیلهای وابسته ارایه گردد |  | 1402-2294-223974 | 1402/06/06 | در مدارک سازه اعمال خواهد شد
13 | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
19
20 | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
21 | Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
22
23 | Date: |  |  |  |  | Date: