## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | 21 | از | 1 | شماره صفحه:
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0011 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR CONTROL/REGULATOR VALVES نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | NOV.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | JUL.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  | MAY.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D00 |  | JUN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F9Z-708932
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | 21 |  | از | 2 | شماره صفحه:
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0011 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 |  | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | X |  | X |  |  |  | 71
8 | X | X | X |  | X |  |  |  | 72
9 | X | X | X |  | X |  |  |  | 73
10 | X | X | X |  | X |  |  |  | 74
11 | X | X | X |  | X |  |  |  | 75
12 | X | X | X |  | X |  |  |  | 76
13 | X | X | X |  | X |  |  |  | 77
14 | X | X | X |  | X |  |  |  | 78
15 | X | X | X |  | X |  |  |  | 79
16 | X | X | X |  | X |  |  |  | 80
17 | X | X | X |  | X |  |  |  | 81
18 | X | X | X |  | X |  |  |  | 82
19 |  | X | X |  | X |  |  |  | 83
20 |  |  | X |  | X |  |  |  | 84
21 |  |  | X |  | X |  |  |  | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | 21 | از | 3 | شماره صفحه:
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0011 | D03
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Specification For Control Valves | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0005
|  | Calculation Note For Control Valve Sizing | [6 empty] | BK-GCS-PEDCO-120-PR-CN-0006

## Notes
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | 21 | از | 4 | شماره صفحه:
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0011 | D03
GENERAL NOTES:
1-The electrical equipment shall be suitable for hazardous area Zone 2, gas group IIB, temperature class T4.
2-Flow direction shall be specified on the valve body.
3- All flanges shall be in accordance with ASME B16.5.
4- Each valve shall be furnished with name plate as per "specification for control valves" with No. "BK-GNRAL-PEDCO-000-IN-SP-0002 ".
5- The following items shall be considered:
- Design standard for globe valves: ips-m-in-160, bs1873
- Design standard for plug valves: ips-m-in-160 api 599
- Valve bonnet and bottom flanges shall be of botled construction with fully retained gaskets
- Trim and seat shall be easily replaceable. seat should be damped or backed up by a seat retainer
- Packing material / packing construction: teflon/chevron type
- Material test certificate
- Dimentional check
- Hydrostatic test
- Performance and mechanical operation test
- Testy certificate including pressure test, visual, dimentional and nude
- Seal leakage test
- Casting examination for valves 6 inches and larger in class 600 and higher as per ansi b 16.34
- Casting quality valves shall ndt(rt tested)
- Mill test certificate for all metallic parts
6- Screwed bolt-type limit stops, e.g. on the control valve stem, adjustable over the full length of the stroke shall be applied. the vendor shall set the limit/travel stops at the required minimum or maximum valve opening.
7- 2 Nos. Eye-Bolt and 2 Nos. Jack Bolt for each valve to be supplied by vendor.
8 - Environmental condition for field instrumentation of Binak Oilfield shall be considered as per the followings:
| • Minimum winter dry bulb: 0.0 °C • Maximum winter relative humidity: 100 • Buildings heating, design dry bulb: 6.0 °C • Design winter dry bulb: -1.0 °C • Design winter relative humidity: 100% • Maximum summer dry bulb: 50.26°C • Maximum summer relative humidity: 100% • Buildings cooling, design dry bulb: 41.0 °C | [5 empty] | • Design summer dry bulb: 77.0 °C • Maximum sun temperature: 85.0 °C • Maximum Shade Temperature: 52.0 °C • Minimum Design relative humidity: 0 • Min. average ambient temperature (°C): 8.35 °C • Max. Average ambient temperature (°C): 35 °C • Min .Absolut air temperature(°C): 0 °C • Max .Absolut air temperature(°C): 47.09 °C
Relative Humidity:
• Maximum Range: 92.27% • Average Relative Humidity 54.7% • Minimum Relative Humidity: 34.94%
9- All Control valves shall be IP 65 and weather proof.
10- Standard ISA75.01 for sizing of Control valves shall be considered by vendor.
11- In accordance to IPS-E-IN-160, Control valve body size normally shall not be less than half of normal line size.
12- Quick Change Trim type control valve to be designed by vendor.
13- Main parameters such as Noise level, vibration, actuator sizing, valve construction material, CV factor, Fluid specification, … to be specified as per standard by vendor.
14- The stroking time shall be lower than 5 second for valves up to 4” and 1 second per inch diameter for bigger ones. (VTC)
15- Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4.5 barg, and the maximum operating pressure is 8 barg. The capacity of the secured instrument air buffer vessel shall be sized for a minimum instrument air supply pressure of 3 barg.
16- Body color of valves shall be selected same as pipe color and actuator shall be green . For more details refer to the latest revision of "Specification For Painting Doc No."BK-GNRAL-PEDCO-000-PI-SP-0006 ".
17- As per IPS-IN-160 test pressures shall be determined by the following relationships:
a) Shell test: 1.5 × maximum permissible, working pressure at 20°C.
b) Disk strength test (applicable to valves 14 inches and larger): 1.5 × maximum permissible working pressure at 20°C.
c) Seat test: 1.1 × maximum permissible working pressure at 20°C.
18- The software using for sizing control valves is Fisher.

## FCV-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 5 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR FLOW CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | FCV-2101
|  |  | 2 | Service | [10 empty] | Gas Compression Inlet Gas Pipeline (Binak)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0001-AN07-6"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0002-D07
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AN07 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 6" | [7 empty] | ASTM A106 Gr.B , B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 18.2
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 7220.4928 |  |  | 6564.084 |  |  |  | 1969.23
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 6.5 |  |  | 6.5 |  |  |  | 6.5
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 1 |  |  | 1 |  |  |  | 1
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 46.11 |  |  | 46.11 |  |  |  | 46.11
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 0.90897
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | -/0.91
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.012 / - / -
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.225 / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | - | [8 empty] | 0.90897
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 106.0964
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 104.857 |  |  | 95.156 |  |  |  | 28.427
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 65 |  |  | 63 |  |  |  | 39
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 4" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 4" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## FCV-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 6 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR FLOW CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | FCV-2102
|  |  | 2 | Service | [10 empty] | Gas Compression Inlet Gas Pipeline (Golkhari)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0001-FN07-8"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0003-D07
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN07 | [7 empty] | SCH.100
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 8" | [7 empty] | ASTM A106 Gr.B , B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 90
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 12395.9313 |  |  | 11269.03 |  |  |  | 3380
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 6.5 |  |  | 6.5 |  |  |  | 6.5
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 1 |  |  | 1 |  |  |  | 1
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 32 |  |  | 32 |  |  |  | 32
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 0.81276
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.984 / - / - | [8 empty] | 0.81276
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.011 / - /-
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.26 /- / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 102.1
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 183.637 |  |  | 166.851 |  |  |  | 50.132
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 63 |  |  | 61 |  |  |  | 33
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 6" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 6" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## FCV-2111
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 7 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR FLOW CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | FCV-2111
|  |  | 2 | Service | [10 empty] | Slug Catcher System
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CDH-112-0014-CN05-3"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0004-D07(2/2)
|  |  | 4 | Area Classification | [10 empty] | Zone1, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | CN05 | [7 empty] | SCH.40
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 3" | [7 empty] | ASTM A106 Gr.B , B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Liquid
|  |  | 11 | State | [10 empty] | Liquid
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 47.7
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/hr |  |  |  |  | 7873.8 |  |  | 7158 |  |  |  | 2505.3
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 19.5 |  |  | 19.5 |  |  |  | 19.5
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 1 |  |  | 1 |  |  |  | 1
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 32 |  |  | 32 |  |  |  | 32
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 0.715
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | - / 0.58
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | - / 1.223
|  |  | 22 | Vapour Pressure | [10 empty] | bar-a |  |  |  |  | 6.5
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 220.3
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 10.804 |  |  | 9.817 |  |  |  | 3.43
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 69 |  |  | 64 |  |  |  | 35
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 2" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## LCV-2114
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 8 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR LEVEL CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | LCV-2114
|  |  | 2 | Service | [10 empty] | Gas Compression Inlet Knock Out Drum to Closed Drain
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CDH-111-0019-AS00-2"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0005-D07
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | NOT Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AS00 | [7 empty] | SCH.10S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | NP / 2" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Liquid
|  |  | 11 | State | [10 empty] | Liquid
|  |  | 12 | Shut Off Pressure delta P | [10 empty] | 13.9
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 1119.5286 |  |  | 1017.7533 |  |  |  | 305.326
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 5.3 |  |  | 5.3 |  |  |  | 5.3
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 4.3 |  |  | 4.3 |  |  |  | 4.3
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 36.9 |  |  | 36.9 |  |  |  | 36.9
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 0.842
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | -/0.691
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.143
|  |  | 22 | Vapour Pressure | [10 empty] | bar-a |  |  |  |  | 0.61
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-a |  |  |  |  | 221.413
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 0.186 |  |  | 0.619 |  |  |  | 0.681
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 19 |  |  | 16 |  |  |  | -
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 1 1/2" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 1 1/2" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PCV-2135A
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 9 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR PRESSURE CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2135A
|  |  | 2 | Service | [10 empty] | 2nd Stage Gas Compression Air Coolers (C-2102A)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0057A-FS00-4"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011-D07(1/3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | IS / 4" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 62.4
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 9530 |  |  | 8664 |  |  |  | 2166
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 54.1 |  |  | 54.1 |  |  |  | 54.1
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 53.6 |  |  | 53.6 |  |  |  | 53.6
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 60 |  |  | 60 |  |  |  | 60
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | -/0.847
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.860 / - / -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.014/ - / -
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.457 / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.65
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 11.447 |  |  | 10.406 |  |  |  | 2.231
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 51 |  |  | 49 |  |  |  | 11
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 3" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 3" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL OPEN |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PCV-2135B
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 10 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR PRESSURE CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2135B
|  |  | 2 | Service | [10 empty] | 2nd Stage Gas Compression Air Coolers (C-2102B)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0057B-FS00-4"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011-D07(2/3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | IS / 4" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 62.4
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 9530 |  |  | 8664 |  |  |  | 2166
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 54.1 |  |  | 54.1 |  |  |  | 54.1
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 53.6 |  |  | 53.6 |  |  |  | 53.6
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 60 |  |  | 60 |  |  |  | 60
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | -/0.847
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.860 / - / -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.014/ - / -
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.457 / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.65
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 11.447 |  |  | 10.406 |  |  |  | 2.231
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 51 |  |  | 49 |  |  |  | 11
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 3" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 3" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL OPEN |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03
D03

## PCV-2135C
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 11 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR PRESSURE CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2135C
|  |  | 2 | Service | [10 empty] | 2nd Stage Gas Compression Air Coolers (C-2102C)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0057C-FS00-4"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011-D07(3/3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | IS / 4" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 62.4
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 9530 |  |  | 8664 |  |  |  | 2166
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 54.1 |  |  | 54.1 |  |  |  | 54.1
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 53.6 |  |  | 53.6 |  |  |  | 53.6
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 60 |  |  | 60 |  |  |  | 60
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | -/0.847
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.860 / - / -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.014/ - / -
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.457 / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.65
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 11.447 |  |  | 10.406 |  |  |  | 2.231
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 51 |  |  | 49 |  |  |  | 11
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 3" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 3" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL OPEN |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PCV-2151
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 12 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR PRESSURE CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2151
|  |  | 2 | Service | [10 empty] | Gas Compression Dehydration Package
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0179-FN05-6"-IS | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0013-D07 (1/3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | IS / 6" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 90
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 18887.886 |  |  | 17170.81 |  |  |  | 5151.3
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 52.9 |  |  | 52.9 |  |  |  | 52.9
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 1 |  |  | 1 |  |  |  | 1
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 59.36 |  |  | 59.36 |  |  |  | 59.42
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 0.847/-
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.9 / -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.0141 / - / -
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.456 / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 104.9
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 96.547 |  |  | 87.644 |  |  |  | 26.124
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 64 |  |  | 62 |  |  |  | 37
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 4" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 4" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PCV-2152
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 13 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR PRESSURE CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2152
|  |  | 2 | Service | [10 empty] | Gas Compression Dehydration Package
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0052-FN05-4"-IS | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0013-D07 (1/3)
|  |  | 4 | Area Classification | [10 empty] | Zone 2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | IS / 4" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 90
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 18887.886 |  |  | 17170.8054 |  |  |  | 5151.3
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 52.9 |  |  | 52.9 |  |  |  | 52.9
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 52.4 |  |  | 52.4 |  |  |  | 52.4
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 59.36 |  |  | 59.36 |  |  |  | 59.36
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 0.847/-
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.9
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.0141 / - / -
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.456 / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 104.9
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 26.114 |  |  | 21.585 |  |  |  | 5.956
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 68 |  |  | 64 |  |  |  | 35
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 3" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 3" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL OPEN |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PCV-2201
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 14 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR PRESSURE CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2201
|  |  | 2 | Service | [10 empty] | Instrument & Plant Air System
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | PLA-112-0010-AN04-1 1/2"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0015-D07 (1/2)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | NOT Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AN04 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 1 1/2" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 18.2
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 42.656 |  |  | 38.7782 |  |  |  | 11.6334
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 9 |  |  | 9 |  |  |  | 9
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 4.5 |  |  | 4.5 |  |  |  | 4.5
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 65 |  |  | 65 |  |  |  | 65
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 1/-
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.998
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.021092
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.41
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 36.7267
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 0.281 |  |  | 0.255 |  |  |  | 0.077
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 65 |  |  | 64 |  |  |  | 43
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 1" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 1" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A 105 | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PCV-2211
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 15 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR PRESSURE CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2211
|  |  | 2 | Service | [10 empty] | Nitrogen Generation System
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | NIT-112-0021-AN01-2"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0016-D07
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | NOT Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AN01 | [7 empty] | SCH.40
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 2" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 18.2
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 42.5 / - / - |  |  | 38.62 / - / - |  |  |  | 11.59/ - / -
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 8 |  |  | 8 |  |  |  | 8
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 0.5 |  |  | 0.5 |  |  |  | 0.5
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 60 |  |  | 60 |  |  |  | 60
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 0.966/-
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.998 / - / -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.01999 / - / -
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.408 / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 32.93
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 0.749 |  |  | 0.681 |  |  |  | 0.204
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 22 |  |  | 19 |  |  |  | -
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 1 1/2" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 1 1/2" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A 105 | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL OPEN |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PCV-2272
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 21 |  | از |  | 16 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D03
DATA SHEETS FOR PRESSURE CONTROL VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2272
|  |  | 2 | Service | [10 empty] | From Inlet K.O. Drum to V-2205
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0004-AN07-3"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0022-D07
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 4.5 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AN07 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 3" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 18.2
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 556.3473 |  |  | 505.8 |  |  |  | 151.731
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 5.1 |  |  | 5.1 |  |  |  | 5.1
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 0.2 |  |  | 0.2 |  |  |  | 0.2
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 37 |  |  | 36.9213 |  |  |  | 37
|  |  | 18 | Specific Gravity (Vapour/water/oil) | [15 empty] | 0.846/-
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.974 / - / -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.01 / - / -
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.245 / -
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.6495
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 19.182 |  |  | 17.423 |  |  |  | 5.206
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 78 |  |  | 75 |  |  |  | 41
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM (Note 6) |  |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 2" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Increase/Decrease Air |  |  |  |  | Increase to Open(VTC)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 ( Note 6) | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | NO. 12 ( Note 8) | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 ( Note 6) | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 ( Note 6) | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 ( Note 6) | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel. Hardened stainless steel or stellited facing shall be supplied
for valve plugs and guides with solid stellited seat rings for Erosice or cavitation/flashing services as per Control valve specification BK- GENRL-PEDCO-000-IN-SP-0005
7- Valve sizing finalized by vendor and client agreement.
8- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PRV-2161
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  |  | 21 | از |  | 17 | شماره صفحه :
9038 – 073 - 053 |  |  | BK | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  | D03
DATA SHEETS FOR PRESSURE REGULATOR VALVES
GENERAL | 1 | Tag No. | [12 empty] | PRV-2161
| 2 | Service | [12 empty] | TK-2102
| 3 | P & ID No. | [12 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D07
| 4 | Area Classification | [12 empty] | Zone2, IIB T4
| 5 | Line No. | [6 empty] | Piping Class | [5 empty] | NIT-112-0010-AN01-1"-PT | [5 empty] | AN01
| 6 | Ambient Temperature | [5 empty] | ⁰C | Min. |  |  | Max. |  |  | 5 | [5 empty] | 50
| 7 | Nace Requirement: | [12 empty] | NO
PROCESS CONDITIONS | 8 | Fluid | [6 empty] | Phase | [5 empty] | NITROGEN | [6 empty] | GAS
| 9 | [13 empty] | Min. Flow |  |  | Norm. Flow |  |  |  | Max. Flow |  |  | Unit
| 10 | Flow Rate | [12 empty] | 3.091 |  |  | 15.5362 |  |  |  | 20.1971 |  |  | Kg/h
| 11 | Inlet Pressure | [12 empty] | 0.05 |  |  | 0.05 |  |  |  | 0.05 |  |  | bar-g
| 12 | Outlet Pressure | [12 empty] | 0 |  |  | 0 |  |  |  | 0 |  |  | bar-g
| 13 | Inlet Temperature | [12 empty] | 60 |  |  | 60 |  |  |  | 60 |  |  | ° C
| 14 | Molecular Weight | [12 empty] | 28.01 |  |  | 28.01 |  |  |  | 28.01 |  |  | -
| 15 | Density | [12 empty] | 1.0755 |  |  | 1.0755 |  |  |  | 1.0755 |  |  | kg/m3
| 16 | Viscosity | [12 empty] | 0.01988 |  |  | 0.01988 |  |  |  | 0.01988 |  |  | Cp
| 17 | Design Temperature | [12 empty] | 85 | [9 empty] | ° C
| 18 | Design Pressure | [12 empty] | 18.2 | [9 empty] | bar-g
| 19 | Calculated Cv / Travel | [12 empty] | 0.005/2.513/3.267 24/59/66 | [9 empty] | - / %
| 20 | Allowable / Predicted SPL | [12 empty] | MAX 85 dBA(VTC) | [9 empty] | dBA
| 21 | Compressibility Factor (Z) | [12 empty] | 0.998
| 22 | Spec. Heat Ratio (K=Cp/Cv) | [12 empty] | 1.408
LINE | 23 | Pipe Line Size |  |  |  |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR |  | 55 | Type |  |  |  |  | Self-actuated regulator
| 24 | Pipe Line Schedule |  |  |  |  | In | Out | SCH. 80 |  |  | SCH.80 |  |  |  |  | 56 | Pilot |  |  |  |  | N/A
| 25 | Pipe Line Insulation/Spec | [6 empty] | PAINTING | [7 empty] | 57 | Supply to Pilot |  |  |  |  | N/A
| 26 | [15 empty] | 58 | Spring Range (bar-g) |  |  |  |  | VTA
VALVE BODY / BONNET | 27 | Body Type | [6 empty] | GLOBE | [7 empty] | 59 | Setpoint (bar-g) |  |  |  |  | 50mbarg
| 28 | Size |  |  | ANSI Class |  |  |  | 1" (Note1) |  |  | 300# |  |  |  |  | 60 | Process Connection |  |  |  |  | 1/2" NPTF (Note1)
| 29 | Mfr. & Model | [6 empty] | VTA | [7 empty] | 61 | Air Failure |  |  |  |  | N/A
| 30 | Body / Bonnet Material | [6 empty] | ASTM A 105 | [7 empty] | 62 | Spring Action |  |  |  |  | N/A
| 31 | End Connection |  |  |  |  | In | Out | 1" (Note1) |  |  | 1" (Note1) |  |  |  |  | 63
| 32 | Type Of Bonnet | [6 empty] | STANDARD | [7 empty] | 64
| 33 | Packing Material | [6 empty] | PTFE | [7 empty] | 65
| 34 | [13 empty] | POSITIONER |  | 66 | Type |  |  |  |  | N/A
| 35 | [15 empty] | 67 | Mfr. & Model |  |  |  |  | N/A
| 36 | [15 empty] | 68 | Input Signal |  | Output Signal |  |  | N/A |  | N/A
TRIM | 37 | Characteristics | [6 empty] | LINEAR (Note1) | [7 empty] | 69 | On Incr Signal Output Incr / Decr |  |  |  |  | N/A
| 38 | Rated |  |  |  | Cv | FL | XT | VTA |  | VTA |  | VTA |  |  |  | 70 | [5 empty] | N/A
| 39 | Trim Material | [6 empty] | SS316 ( Note 4 ) | [7 empty] | 71 | Electrical Connection |  |  |  |  | N/A
| 40 | Seat Material | [6 empty] | NO. 12 ( Note 5 ) | [7 empty] | 72 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 41 | Req. Seat Tightness | [6 empty] | Class IV | [5 empty] | LIMIT SWITCH |  | 73 | Type |  | Quantity |  |  | N/A |  | N/A
| 42 | [15 empty] | 74 | Mfr. & Model |  |  |  |  | N/A
| 43 | [15 empty] | 75 | Tag Number(s) |  |  |  |  | N/A
PURCHASE | 44 | Manufacturer | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 76 | Actuation Point |  |  |  |  | N/A
| 45 | Model | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 77 | Contacts / Rating |  |  |  |  | N/A
SOLENOID VALVE | 46 | Type | [6 empty] | N/A | [7 empty] | 78 | Electrical Connection |  |  |  |  | N/A
| 47 | Tag Number | [6 empty] | N/A | [7 empty] | 79 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 48 | Body Material | [6 empty] | N/A | [5 empty] | AIR SET |  | 80 | Mfr. & Model |  |  |  |  | VTA
| 49 | Operating Voltage | [6 empty] | N/A | [7 empty] | 81 | Set Pressure |  |  |  |  | VTA
| 50 | Elec. Connection | [6 empty] | N/A | [7 empty] | 82 | Filter |  | Gauges |  |  | VTA | VTA
| 51 | Manual Reset | [6 empty] | N/A | [7 empty] | 83 | Pneumatic Connection |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | Ingress Protection |  |  |  | N/A |  | N/A |  |  |  | TESTS |  | 84 | Hydro Pressure |  |  |  |  | YES
SPECIAL ACCESSORIES | 53 | Fusible Leakage |  |  | Booster |  |  | - | N/A |  | N/A | [5 empty] | 85 | NACE MR 0175 |  |  |  |  | No
| 54 | Block Relay |  |  | Volume Tank |  |  | - | N/A |  | N/A | [5 empty] | 86
Notes:
VTA: Vendor To Advise N/A: Not Applicable
1- Shall be confirmed by vendor.
2- Shall be stated by vendor at quotaion stage.
3- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
4- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel.
5- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PRV-2162
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  |  | 21 | از |  | 18 | شماره صفحه :
9038 – 073 - 053 |  |  | BK | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  | D03
DATA SHEETS FOR PRESSURE REGULATOR VALVES
GENERAL | 1 | Tag No. | [12 empty] | PRV-2162
| 2 | Service | [12 empty] | From Nitrogen Header to TK-2102
| 3 | P & ID No. | [12 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D07
| 4 | Area Classification | [12 empty] | Zone2, IIB T4
| 5 | Line No. | [6 empty] | Piping Class | [5 empty] | NIT-112-0010-AN01-1"-PT | [5 empty] | AN01
| 6 | Ambient Temperature | [5 empty] | ⁰C | Min. |  |  | Max. |  |  | 5 | [5 empty] | 50
| 7 | Nace Requirement: | [12 empty] | NO
PROCESS CONDITIONS | 8 | Fluid | [6 empty] | Phase | [5 empty] | NITROGEN | [6 empty] | GAS
| 9 | [13 empty] | Min. Flow |  |  | Norm. Flow |  |  |  | Max. Flow |  |  | Unit
| 10 | Flow Rate | [12 empty] | 6.1959 |  |  | 17.8692 |  |  |  | 23.23 |  |  | Kg/h
| 11 | Inlet Pressure | [12 empty] | 7.5 |  |  | 7.5 |  |  |  | 7.5 |  |  | bar-g
| 12 | Outlet Pressure | [12 empty] | 7.49 |  |  | 7.49 |  |  |  | 7.49 |  |  | bar-g
| 13 | Inlet Temperature | [12 empty] | 60 |  |  | 60 |  |  |  | 60 |  |  | ° C
| 14 | Molecular Weight | [12 empty] | 28.01 |  |  | 28.01 |  |  |  | 28.01 |  |  | -
| 15 | Density | [12 empty] | 8.62 |  |  | 8.62 |  |  |  | 8.62 |  |  | kg/m3
| 16 | Viscosity | [12 empty] | 0.01988 |  |  | 0.01988 |  |  |  | 0.01988 |  |  | Cp
| 17 | Design Temperature | [12 empty] | 85 | [9 empty] | ° C
| 18 | Design Pressure | [12 empty] | 18.2 | [9 empty] | bar-g
| 19 | Calculated Cv / Travel | [12 empty] | 0.048/0.139/0.180 54/50/29 | [9 empty] | - / %
| 20 | Allowable / Predicted SPL | [12 empty] | MAX 85 dBA(VTC) | [9 empty] | dBA
| 21 | Compressibility Factor (Z) | [12 empty] | 0.998
| 22 | Spec. Heat Ratio (K=Cp/Cv) | [12 empty] | 1.408
LINE | 23 | Pipe Line Size |  |  |  |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR |  | 55 | Type |  |  |  |  | Self-actuated regulator
| 24 | Pipe Line Schedule |  |  |  |  | In | Out | SCH. 80 |  |  | SCH.80 |  |  |  |  | 56 | Pilot |  |  |  |  | N/A
| 25 | Pipe Line Insulation/Spec | [6 empty] | PAINTING | [7 empty] | 57 | Supply to Pilot |  |  |  |  | N/A
| 26 | [15 empty] | 58 | Spring Range (bar-g) |  |  |  |  | VTA
VALVE BODY / BONNET | 27 | Body Type | [6 empty] | GLOBE | [7 empty] | 59 | Setpoint (bar-g) |  |  |  |  | 10mbarg
| 28 | Size |  |  | ANSI Class |  |  |  | 1" (Note1) |  |  | 300# |  |  |  |  | 60 | Process Connection |  |  |  |  | 1/2" NPTF (Note1)
| 29 | Mfr. & Model | [6 empty] | VTA | [7 empty] | 61 | Air Failure |  |  |  |  | N/A
| 30 | Body / Bonnet Material | [6 empty] | ASTM A 105 | [7 empty] | 62 | Spring Action |  |  |  |  | N/A
| 31 | End Connection |  |  |  |  | In | Out | 1" (Note1) |  |  | 1" (Note1) |  |  |  |  | 63
| 32 | Type Of Bonnet | [6 empty] | STANDARD | [7 empty] | 64
| 33 | Packing Material | [6 empty] | PTFE | [7 empty] | 65
| 34 | [13 empty] | POSITIONER |  | 66 | Type |  |  |  |  | N/A
| 35 | [15 empty] | 67 | Mfr. & Model |  |  |  |  | N/A
| 36 | [15 empty] | 68 | Input Signal |  | Output Signal |  |  | N/A |  | N/A
TRIM | 37 | Characteristics | [6 empty] | LINEAR (Note1) | [7 empty] | 69 | On Incr Signal Output Incr / Decr |  |  |  |  | N/A
| 38 | Rated |  |  |  | Cv | FL | XT | VTA |  | VTA |  | VTA |  |  |  | 70 | [5 empty] | N/A
| 39 | Trim Material | [6 empty] | SS316 ( Note 4 ) | [7 empty] | 71 | Electrical Connection |  |  |  |  | N/A
| 40 | Seat Material | [6 empty] | NO. 12 ( Note 5 ) | [7 empty] | 72 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 41 | Req. Seat Tightness | [6 empty] | Class IV | [5 empty] | LIMIT SWITCH |  | 73 | Type |  | Quantity |  |  | N/A |  | N/A
| 42 | [15 empty] | 74 | Mfr. & Model |  |  |  |  | N/A
| 43 | [15 empty] | 75 | Tag Number(s) |  |  |  |  | N/A
PURCHASE | 44 | Manufacturer | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 76 | Actuation Point |  |  |  |  | N/A
| 45 | Model | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 77 | Contacts / Rating |  |  |  |  | N/A
SOLENOID VALVE | 46 | Type | [6 empty] | N/A | [7 empty] | 78 | Electrical Connection |  |  |  |  | N/A
| 47 | Tag Number | [6 empty] | N/A | [7 empty] | 79 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 48 | Body Material | [6 empty] | N/A | [5 empty] | AIR SET |  | 80 | Mfr. & Model |  |  |  |  | VTA
| 49 | Operating Voltage | [6 empty] | N/A | [7 empty] | 81 | Set Pressure |  |  |  |  | VTA
| 50 | Elec. Connection | [6 empty] | N/A | [7 empty] | 82 | Filter |  | Gauges |  |  | VTA | VTA
| 51 | Manual Reset | [6 empty] | N/A | [7 empty] | 83 | Pneumatic Connection |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | Ingress Protection |  |  |  | N/A |  | N/A |  |  |  | TESTS |  | 84 | Hydro Pressure |  |  |  |  | YES
SPECIAL ACCESSORIES | 53 | Fusible Leakage |  |  | Booster |  |  | - | N/A |  | N/A | [5 empty] | 85 | NACE MR 0175 |  |  |  |  | No
| 54 | Block Relay |  |  | Volume Tank |  |  | - | N/A |  | N/A | [5 empty] | 86
Notes:
VTA: Vendor To Advise N/A: Not Applicable
1- Shall be confirmed by vendor.
2- Shall be stated by vendor at quotaion stage.
3- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
4- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel.
5- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PRV-2201
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  |  | 21 | از |  | 19 | شماره صفحه :
9038 – 073 - 053 |  |  | BK | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  | D03
DATA SHEETS FOR PRESSURE REGULATOR VALVES
GENERAL | 1 | Tag No. | [12 empty] | PRV-2201
| 2 | Service | [12 empty] | From Air Dryer Package (Pk-Dr-2203)
| 3 | P & ID No. | [12 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D07 (2/2)
| 4 | Area Classification | [12 empty] | Zone2, IIB T4
| 5 | Line No. | [6 empty] | Piping Class | [5 empty] | ISA-112-0112-AZ00-2"-NP | [5 empty] | AZ00
| 6 | Ambient Temperature | [5 empty] | ⁰C | Min. |  |  | Max. |  |  | 5 | [5 empty] | 50
| 7 | Nace Requirement: | [12 empty] | NO
PROCESS CONDITIONS | 8 | Fluid | [6 empty] | Phase | [5 empty] | AIR | [6 empty] | GAS
| 9 | [13 empty] | Min. Flow |  |  | Norm. Flow |  |  |  | Max. Flow |  |  | Unit
| 10 | Flow Rate | [12 empty] | 35.664 |  |  | 118.881 |  |  |  | 154.607 |  |  | Kg/h
| 11 | Inlet Pressure | [12 empty] | 9 |  |  | 9 |  |  |  | 9 |  |  | bar-g
| 12 | Outlet Pressure | [12 empty] | 8 |  |  | 8 |  |  |  | 8 |  |  | bar-g
| 13 | Inlet Temperature | [12 empty] | 65 |  |  | 65 |  |  |  | 65 |  |  | ° C
| 14 | Molecular Weight | [12 empty] | 28.97 |  |  | 28.97 |  |  |  | 28.97 |  |  | -
| 15 | Density | [12 empty] | 10.3314 |  |  | 10.3314 |  |  |  | 10.3314 |  |  | kg/m3
| 16 | Viscosity | [12 empty] | 0.021092 |  |  | 0.021092 |  |  |  | 0.021092 |  |  | Cp
| 17 | Design Temperature | [12 empty] | 85 | [9 empty] | ° C
| 18 | Design Pressure | [12 empty] | 18.2 | [9 empty] | bar-g
| 19 | Calculated Cv / Travel | [12 empty] | 0.427/1.424/1.852 25/42/52 | [9 empty] | - / %
| 20 | Allowable / Predicted SPL | [12 empty] | MAX 85 dBA(VTC) | [9 empty] | dBA
| 21 | Compressibility Factor (Z) | [12 empty] | 0.998
| 22 | Spec. Heat Ratio (K=Cp/Cv) | [12 empty] | 1.4
LINE | 23 | Pipe Line Size |  |  |  |  | In | Out | 2" |  |  | 2" |  |  | ACTUATOR |  | 55 | Type |  |  |  |  | Self-actuated regulator
| 24 | Pipe Line Schedule |  |  |  |  | In | Out | SCH. 40 |  |  | SCH.40 |  |  |  |  | 56 | Pilot |  |  |  |  | N/A
| 25 | Pipe Line Insulation/Spec | [6 empty] | PAINTING | [7 empty] | 57 | Supply to Pilot |  |  |  |  | N/A
| 26 | [15 empty] | 58 | Spring Range (bar-g) |  |  |  |  | VTA
VALVE BODY / BONNET | 27 | Body Type | [6 empty] | GLOBE | [7 empty] | 59 | Setpoint (bar-g) |  |  |  |  | 8barg
| 28 | Size |  |  | ANSI Class |  |  |  | 1 1/2" (Note1) |  |  | 300# |  |  |  |  | 60 | Process Connection |  |  |  |  | 1/2" NPTF (Note1)
| 29 | Mfr. & Model | [6 empty] | VTA | [7 empty] | 61 | Air Failure |  |  |  |  | N/A
| 30 | Body / Bonnet Material | [6 empty] | ASTM B148 UNS C95800 | [7 empty] | 62 | Spring Action |  |  |  |  | N/A
| 31 | End Connection |  |  |  |  | In | Out | 2" (Note1) |  |  | 2" (Note1) |  |  |  |  | 63
| 32 | Type Of Bonnet | [6 empty] | STANDARD | [7 empty] | 64
| 33 | Packing Material | [6 empty] | PTFE | [7 empty] | 65
| 34 | [13 empty] | POSITIONER |  | 66 | Type |  |  |  |  | N/A
| 35 | [15 empty] | 67 | Mfr. & Model |  |  |  |  | N/A
| 36 | [15 empty] | 68 | Input Signal |  | Output Signal |  |  | N/A |  | N/A
TRIM | 37 | Characteristics | [6 empty] | LINEAR (Note1) | [7 empty] | 69 | On Incr Signal Output Incr / Decr |  |  |  |  | N/A
| 38 | Rated |  |  |  | Cv | FL | XT | VTA |  | VTA |  | VTA |  |  |  | 70 | [5 empty] | N/A
| 39 | Trim Material | [6 empty] | SS316 ( Note 4 ) | [7 empty] | 71 | Electrical Connection |  |  |  |  | N/A
| 40 | Seat Material | [6 empty] | NO. 12 ( Note 5 ) | [7 empty] | 72 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 41 | Req. Seat Tightness | [6 empty] | Class IV | [5 empty] | LIMIT SWITCH |  | 73 | Type |  | Quantity |  |  | N/A |  | N/A
| 42 | [15 empty] | 74 | Mfr. & Model |  |  |  |  | N/A
| 43 | [15 empty] | 75 | Tag Number(s) |  |  |  |  | N/A
PURCHASE | 44 | Manufacturer | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 76 | Actuation Point |  |  |  |  | N/A
| 45 | Model | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 77 | Contacts / Rating |  |  |  |  | N/A
SOLENOID VALVE | 46 | Type | [6 empty] | N/A | [7 empty] | 78 | Electrical Connection |  |  |  |  | N/A
| 47 | Tag Number | [6 empty] | N/A | [7 empty] | 79 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 48 | Body Material | [6 empty] | N/A | [5 empty] | AIR SET |  | 80 | Mfr. & Model |  |  |  |  | VTA
| 49 | Operating Voltage | [6 empty] | N/A | [7 empty] | 81 | Set Pressure |  |  |  |  | VTA
| 50 | Elec. Connection | [6 empty] | N/A | [7 empty] | 82 | Filter |  | Gauges |  |  | VTA | VTA
| 51 | Manual Reset | [6 empty] | N/A | [7 empty] | 83 | Pneumatic Connection |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | Ingress Protection |  |  |  | N/A |  | N/A |  |  |  | TESTS |  | 84 | Hydro Pressure |  |  |  |  | YES
SPECIAL ACCESSORIES | 53 | Fusible Leakage |  |  | Booster |  |  | - | N/A |  | N/A | [5 empty] | 85 | NACE MR 0175 |  |  |  |  | No
| 54 | Block Relay |  |  | Volume Tank |  |  | - | N/A |  | N/A | [5 empty] | 86
Notes:
VTA: Vendor To Advise N/A: Not Applicable
1- Shall be confirmed by vendor.
2- Shall be stated by vendor at quotaion stage.
3- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
4- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel.
5- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PRV-2291
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  |  | 21 | از |  | 20 | شماره صفحه :
9038 – 073 - 053 |  |  | BK | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  | D03
DATA SHEETS FOR PRESSURE REGULATOR VALVES
GENERAL | 1 | Tag No. | [12 empty] | PRV-2291
| 2 | Service | [12 empty] | From Nitrogen Header to V-2107
| 3 | P & ID No. | [12 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D07
| 4 | Area Classification | [12 empty] | Zone2, IIB T4
| 5 | Line No. | [6 empty] | Piping Class | [5 empty] | NIT-111-0005-AN01-1"-PT | [5 empty] | AN01
| 6 | Ambient Temperature | [5 empty] | ⁰C | Min. |  |  | Max. |  |  | 5 | [5 empty] | 50
| 7 | Nace Requirement: | [12 empty] | NO
PROCESS CONDITIONS | 8 | Fluid | [6 empty] | Phase | [5 empty] | NITROGEN | [6 empty] | GAS
| 9 | [13 empty] | Min. Flow |  |  | Norm. Flow |  |  |  | Max. Flow |  |  | Unit
| 10 | Flow Rate | [12 empty] | 0.74 |  |  | 6.37 |  |  |  | 6.94 |  |  | Kg/h
| 11 | Inlet Pressure | [12 empty] | 7.5 |  |  | 7.5 |  |  |  | 7.5 |  |  | bar-g
| 12 | Outlet Pressure | [12 empty] | 0.01 |  |  | 0.01 |  |  |  | 0.01 |  |  | bar-g
| 13 | Inlet Temperature | [12 empty] | 60 |  |  | 60 |  |  |  | 60 |  |  | ° C
| 14 | Molecular Weight | [12 empty] | 28.01 |  |  | 28.01 |  |  |  | 28.01 |  |  | -
| 15 | Density | [12 empty] | 8.62 |  |  | 8.62 |  |  |  | 8.62 |  |  | kg/m3
| 16 | Viscosity | [12 empty] | 0.01988 |  |  | 0.01988 |  |  |  | 0.01988 |  |  | Cp
| 17 | Design Temperature | [12 empty] | 85 | [9 empty] | ° C
| 18 | Design Pressure | [12 empty] | 18.2 | [9 empty] | bar-g
| 19 | Calculated Cv / Travel | [12 empty] | 0.0066/0.054/0.059 81/46/49 | [9 empty] | - / %
| 20 | Allowable / Predicted SPL | [12 empty] | MAX 85 dBA(VTC) | [9 empty] | dBA
| 21 | Compressibility Factor (Z) | [12 empty] | 0.998
| 22 | Spec. Heat Ratio (K=Cp/Cv) | [12 empty] | 1.408
LINE | 23 | Pipe Line Size |  |  |  |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR |  | 55 | Type |  |  |  |  | Self-actuated regulator
| 24 | Pipe Line Schedule |  |  |  |  | In | Out | SCH. 80 |  |  | SCH.80 |  |  |  |  | 56 | Pilot |  |  |  |  | N/A
| 25 | Pipe Line Insulation/Spec | [6 empty] | PAINTING | [7 empty] | 57 | Supply to Pilot |  |  |  |  | N/A
| 26 | [15 empty] | 58 | Spring Range (bar-g) |  |  |  |  | VTA
VALVE BODY / BONNET | 27 | Body Type | [6 empty] | GLOBE | [7 empty] | 59 | Setpoint (bar-g) |  |  |  |  | 10mbarg
| 28 | Size |  |  | ANSI Class |  |  |  | 1" (Note1) |  |  | 300# |  |  |  |  | 60 | Process Connection |  |  |  |  | 1/2" NPTF (Note1)
| 29 | Mfr. & Model | [6 empty] | VTA | [7 empty] | 61 | Air Failure |  |  |  |  | N/A
| 30 | Body / Bonnet Material | [6 empty] | ASTM A 105 | [7 empty] | 62 | Spring Action |  |  |  |  | N/A
| 31 | End Connection |  |  |  |  | In | Out | 1" (Note1) |  |  | 1" (Note1) |  |  |  |  | 63
| 32 | Type Of Bonnet | [6 empty] | STANDARD | [7 empty] | 64
| 33 | Packing Material | [6 empty] | PTFE | [7 empty] | 65
| 34 | [13 empty] | POSITIONER |  | 66 | Type |  |  |  |  | N/A
| 35 | [15 empty] | 67 | Mfr. & Model |  |  |  |  | N/A
| 36 | [15 empty] | 68 | Input Signal |  | Output Signal |  |  | N/A |  | N/A
TRIM | 37 | Characteristics | [6 empty] | LINEAR (Note1) | [7 empty] | 69 | On Incr Signal Output Incr / Decr |  |  |  |  | N/A
| 38 | Rated |  |  |  | Cv | FL | XT | VTA |  | VTA |  | VTA |  |  |  | 70 | [5 empty] | N/A
| 39 | Trim Material | [6 empty] | SS316 ( Note 4 ) | [7 empty] | 71 | Electrical Connection |  |  |  |  | N/A
| 40 | Seat Material | [6 empty] | NO. 12 ( Note 5 ) | [7 empty] | 72 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 41 | Req. Seat Tightness | [6 empty] | Class IV | [5 empty] | LIMIT SWITCH |  | 73 | Type |  | Quantity |  |  | N/A |  | N/A
| 42 | [15 empty] | 74 | Mfr. & Model |  |  |  |  | N/A
| 43 | [15 empty] | 75 | Tag Number(s) |  |  |  |  | N/A
PURCHASE | 44 | Manufacturer | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 76 | Actuation Point |  |  |  |  | N/A
| 45 | Model | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 77 | Contacts / Rating |  |  |  |  | N/A
SOLENOID VALVE | 46 | Type | [6 empty] | N/A | [7 empty] | 78 | Electrical Connection |  |  |  |  | N/A
| 47 | Tag Number | [6 empty] | N/A | [7 empty] | 79 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 48 | Body Material | [6 empty] | N/A | [5 empty] | AIR SET |  | 80 | Mfr. & Model |  |  |  |  | VTA
| 49 | Operating Voltage | [6 empty] | N/A | [7 empty] | 81 | Set Pressure |  |  |  |  | VTA
| 50 | Elec. Connection | [6 empty] | N/A | [7 empty] | 82 | Filter |  | Gauges |  |  | VTA | VTA
| 51 | Manual Reset | [6 empty] | N/A | [7 empty] | 83 | Pneumatic Connection |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | Ingress Protection |  |  |  | N/A |  | N/A |  |  |  | TESTS |  | 84 | Hydro Pressure |  |  |  |  | YES
SPECIAL ACCESSORIES | 53 | Fusible Leakage |  |  | Booster |  |  | - | N/A |  | N/A | [5 empty] | 85 | NACE MR 0175 |  |  |  |  | No
| 54 | Block Relay |  |  | Volume Tank |  |  | - | N/A |  | N/A | [5 empty] | 86
Notes:
VTA: Vendor To Advise N/A: Not Applicable
1- Shall be confirmed by vendor.
2- Shall be stated by vendor at quotaion stage.
3- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
4- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel.
5- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03

## PRV-2292
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  |  | 21 | از |  | 21 | شماره صفحه :
9038 – 073 - 053 |  |  | BK | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  | D03
DATA SHEETS FOR PRESSURE REGULATOR VALVES
GENERAL | 1 | Tag No. | [12 empty] | PRV-2292
| 2 | Service | [12 empty] | From V-2107 to ATM
| 3 | P & ID No. | [12 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D07
| 4 | Area Classification | [12 empty] | Zone2, IIB T4
| 5 | Line No. | [6 empty] | Piping Class | [5 empty] | NIT-111-0009-AN04-1"-PT | [5 empty] | AN04
| 6 | Ambient Temperature | [5 empty] | ⁰C | Min. |  |  | Max. |  |  | 5 | [5 empty] | 50
| 7 | Nace Requirement: | [12 empty] | YES
PROCESS CONDITIONS | 8 | Fluid | [6 empty] | Phase | [5 empty] | NITROGEN | [6 empty] | GAS
| 9 | [13 empty] | Min. Flow |  |  | Norm. Flow |  |  |  | Max. Flow |  |  | Unit
| 10 | Flow Rate | [12 empty] | 0.74 |  |  | 4.26 |  |  |  | 4.61 |  |  | Kg/h
| 11 | Inlet Pressure | [12 empty] | 0.05 |  |  | 0.05 |  |  |  | 0.05 |  |  | bar-g
| 12 | Outlet Pressure | [12 empty] | 0 |  |  | 0 |  |  |  | 0 |  |  | bar-g
| 13 | Inlet Temperature | [12 empty] | 60 |  |  | 60 |  |  |  | 60 |  |  | ° C
| 14 | Molecular Weight | [12 empty] | 28.01 |  |  | 28.01 |  |  |  | 28.01 |  |  | -
| 15 | Density | [12 empty] | 1.08 |  |  | 1.08 |  |  |  | 1.08 |  |  | kg/m3
| 16 | Viscosity | [12 empty] | 0.01988 |  |  | 0.01988 |  |  |  | 0.01988 |  |  | Cp
| 17 | Design Temperature | [12 empty] | 85 | [9 empty] | ° C
| 18 | Design Pressure | [12 empty] | 18.2 | [9 empty] | bar-g
| 19 | Calculated Cv / Travel | [12 empty] | 0.120/0.689/0.746 -/30/31 | [9 empty] | - / %
| 20 | Allowable / Predicted SPL | [12 empty] | MAX 85 dBA(VTC) | [9 empty] | dBA
| 21 | Compressibility Factor (Z) | [12 empty] | 0.998
| 22 | Spec. Heat Ratio (K=Cp/Cv) | [12 empty] | 1.408
LINE | 23 | Pipe Line Size |  |  |  |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR |  | 55 | Type |  |  |  |  | Self-actuated regulator
| 24 | Pipe Line Schedule |  |  |  |  | In | Out | SCH.XXS |  |  | SCH.XXS |  |  |  |  | 56 | Pilot |  |  |  |  | N/A
| 25 | Pipe Line Insulation/Spec | [6 empty] | PAINTING | [7 empty] | 57 | Supply to Pilot |  |  |  |  | N/A
| 26 | [15 empty] | 58 | Spring Range (bar-g) |  |  |  |  | VTA
VALVE BODY / BONNET | 27 | Body Type | [6 empty] | GLOBE | [7 empty] | 59 | Setpoint (bar-g) |  |  |  |  | 50mbarg
| 28 | Size |  |  | ANSI Class |  |  |  | 1" (Note1) |  |  | 300# |  |  |  |  | 60 | Process Connection |  |  |  |  | 1/2" NPTF (Note1)
| 29 | Mfr. & Model | [6 empty] | VTA | [7 empty] | 61 | Air Failure |  |  |  |  | N/A
| 30 | Body / Bonnet Material | [6 empty] | ASTM A 105 | [7 empty] | 62 | Spring Action |  |  |  |  | N/A
| 31 | End Connection |  |  |  |  | In | Out | 1" (Note1) |  |  | 1" (Note1) |  |  |  |  | 63
| 32 | Type Of Bonnet | [6 empty] | STANDARD | [7 empty] | 64
| 33 | Packing Material | [6 empty] | PTFE | [7 empty] | 65
| 34 | [13 empty] | POSITIONER |  | 66 | Type |  |  |  |  | N/A
| 35 | [15 empty] | 67 | Mfr. & Model |  |  |  |  | N/A
| 36 | [15 empty] | 68 | Input Signal |  | Output Signal |  |  | N/A |  | N/A
TRIM | 37 | Characteristics | [6 empty] | LINEAR (Note1) | [7 empty] | 69 | On Incr Signal Output Incr / Decr |  |  |  |  | N/A
| 38 | Rated |  |  |  | Cv | FL | XT | VTA |  | VTA |  | VTA |  |  |  | 70 | [5 empty] | N/A
| 39 | Trim Material | [6 empty] | SS316 ( Note 4 ) | [7 empty] | 71 | Electrical Connection |  |  |  |  | N/A
| 40 | Seat Material | [6 empty] | NO. 12 ( Note 5 ) | [7 empty] | 72 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 41 | Req. Seat Tightness | [6 empty] | Class IV | [5 empty] | LIMIT SWITCH |  | 73 | Type |  | Quantity |  |  | N/A |  | N/A
| 42 | [15 empty] | 74 | Mfr. & Model |  |  |  |  | N/A
| 43 | [15 empty] | 75 | Tag Number(s) |  |  |  |  | N/A
PURCHASE | 44 | Manufacturer | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 76 | Actuation Point |  |  |  |  | N/A
| 45 | Model | [6 empty] | (NOTE 2 in Below Table) | [7 empty] | 77 | Contacts / Rating |  |  |  |  | N/A
SOLENOID VALVE | 46 | Type | [6 empty] | N/A | [7 empty] | 78 | Electrical Connection |  |  |  |  | N/A
| 47 | Tag Number | [6 empty] | N/A | [7 empty] | 79 | Ex Certificate |  | Ingress Protection |  |  | N/A |  | N/A
| 48 | Body Material | [6 empty] | N/A | [5 empty] | AIR SET |  | 80 | Mfr. & Model |  |  |  |  | VTA
| 49 | Operating Voltage | [6 empty] | N/A | [7 empty] | 81 | Set Pressure |  |  |  |  | VTA
| 50 | Elec. Connection | [6 empty] | N/A | [7 empty] | 82 | Filter |  | Gauges |  |  | VTA | VTA
| 51 | Manual Reset | [6 empty] | N/A | [7 empty] | 83 | Pneumatic Connection |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | Ingress Protection |  |  |  | N/A |  | N/A |  |  |  | TESTS |  | 84 | Hydro Pressure |  |  |  |  | YES
SPECIAL ACCESSORIES | 53 | Fusible Leakage |  |  | Booster |  |  | - | N/A |  | N/A | [5 empty] | 85 | NACE MR 0175 |  |  |  |  | YES
| 54 | Block Relay |  |  | Volume Tank |  |  | - | N/A |  | N/A | [5 empty] | 86
Notes:
VTA: Vendor To Advise N/A: Not Applicable
1- Shall be confirmed by vendor.
2- Shall be stated by vendor at quotaion stage.
3- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
4- Trim part material shall be considered as minimum 316SS and hard face or any equal hard steel.
5- As per Piping Material Specification Doc. No.: "BK-GCS-PEDCO-120-PI-SP-0001", Refer to table 8 of API 600 Rev. 2015.
D03