## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 34
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0009 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | OCT.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | SEP.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAY.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F9Z-708930
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For PURCHASE (will be finalized later)
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از34
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0009 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | X |  | X |  |  |  | 71
8 | X | X | X |  | X |  |  |  | 72
9 | X | X | X |  | X |  |  |  | 73
10 | X | X | X |  | X |  |  |  | 74
11 | X | X | X |  | X |  |  |  | 75
12 | X | X | X |  | X |  |  |  | 76
13 | X | X | X |  | X |  |  |  | 77
14 | X | X | X |  | X |  |  |  | 78
15 | X | X | X |  | X |  |  |  | 79
16 | X | X | X |  | X |  |  |  | 80
17 | X | X | X |  | X |  |  |  | 81
18 | X | X | X |  | X |  |  |  | 82
19 | X | X | X |  | X |  |  |  | 83
20 | X | X | X |  | X |  |  |  | 84
21 | X | X | X |  | X |  |  |  | 85
22 | X | X | X |  | X |  |  |  | 86
23 | X | X | X |  | X |  |  |  | 87
24 | X | X | X |  | X |  |  |  | 88
25 | X | X | X |  | X |  |  |  | 89
26 | X | X | X |  | X |  |  |  | 90
27 | X | X | X |  | X |  |  |  | 91
28 | X | X | X |  | X |  |  |  | 92
29 | X | X | X |  | X |  |  |  | 93
30 | X | X | X |  | X |  |  |  | 94
31 | X | X | X |  | X |  |  |  | 95
32 | X | X | X |  | X |  |  |  | 96
33 | X | X | X |  | X |  |  |  | 97
34 | X | X |  |  | X |  |  |  | 98
35 | X | X | [6 empty] | 99
36 | X | X | [6 empty] | 100
37 | X | X | [6 empty] | 101
38 |  | X | [6 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 34
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0009 | D03
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Specification For Painting | [6 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Specification For Pressure Safety Valves(PSV) | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0007
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## Notes
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 34
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0009 | D03
GENERAL NOTES:
1- All valves shall be clearly and permanently marked. The name plate shall be corrosion resistant Stainless Steel and pinned to the valve body. Wired on labels are not acceptable. Following information shall be submitted on nameplate for approval.
|  | - | Tag number
|  | - | Manufacturer name, model and serial number
|  | - | Set Pressure
|  | - | Pressure rating
|  | - | Body size and material
|  | - | Measurement Range
|  | - | Liquid density
|  | - | Degree of protection & electrical construction
|  | - | Marking as per IEC Codes
|  | - | Well name
2- Calculation sheet using API RP-520 formula shall be provided by vendor for each safety/relief valve in accordance with process values.
3- All wetted part material shall be in accordance with ISO 15156-2 region 2 or NACE MR-01-75 as specified in data sheets for each tag . For these mentioned tags, both the compliance shall be provided.primary and secondary sides of valves shall meet NACE MR-01-75 requirements and certificate of
4- The safety/ relief valves shall comply with API RP 520, 521, 526 and 527 standards. All valves shall be supplied with ASME section VIII.
5- All valves shall be tested for leakage at the manufacturer's works in accordance with API 527. The procedures for these tests shall be submitted for approval.
6- Gasket material shall be suitable for the application.
7-The inlet/outlet sizes & rating and center to flange face dimensions for all valves shall be in accordance with API-526.
8- All the valves with the materials offered shall meet the set pressure and other design conditions for the orifice selected.
9-Vendor to advise all wetted parts materials include disc holder, stem guide, blowdown ring, ring pin, bushing and other internal components in contact with process fluid in bid stage
10 - Environmental condition for field instrumentation of Binak Oilfield shall be considered as per the followings:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB for Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
11 - Material Test Certificate and calibration Certificate for all transmitters to be submitted by Vendor.
12- Body and other pressure parts subject to inlet pressure (primary pressure zone) shall be hydrostatically tested at a pressure of at least 1.5 times the
design pressure of the parts
13- Safety relief valves shall be subject to a seat leakage test in accordance with API standard 527 as applicable, or as agreed upon by the
manufacturer and the CLINET
14- Lifting lever shall be provided whenever the fluid to be relieved, is steam, air, or hot water (60°C and above)
15- Balanced bellows valves shall have open bonnet construction.
16- In valves with balancing bellow, the bonnet shall have a ½” threaded hole, NPT as per ANSI 1.20.1.
17- In bellows type, bonnet shall be vented separately from discharge.
18- Body color of Pressure & Safety Relief Valves shall be yellow. For more details referto the latest revision of Specification For Painting Doc No.
"BK-GNRAL-PEDCO-000-PI-SP-0006",( Paint system 2-A as per table 2 of reference specification is required).
D03

## PSV-2111
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 5 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2111
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0013-AN07-8"-PT | [6 empty] | V-2104
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN07 / 6mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004-D07 (1 of 2)
|  | 5 | Discharge to | [7 empty] | To LP FLARE HEADER
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 37247.2 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 48.1 |  | kg/kmol | [5 empty] | 1.6586 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 5.3 / | [5 empty] | 9 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 32 |  |  | / |  |  | 284 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 3.4 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 3.4 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.954
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 427.9 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.223
|  | 26 | Density @ flowing temprature | [7 empty] | 8.355 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.0108 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | YES
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 4134(VTC)
|  | 34 | Required Area MM² | [7 empty] | 8742 (VTC)
|  | 35 | Orifice Designation | [7 empty] | Q (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 6" |  |  | in |  |  |  |  | 8" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB |  |  |  |  | (VTC)
|  | 39 | Seat and Disc (Trim) | [7 empty] | SS316+PTFE (VTC)
|  | 40 | Nozzle | [7 empty] | SS316 (VTC)
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC)(Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2112
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 6 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2112
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0014-AN07-8"-PT | [6 empty] | V-2104
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN07 / 6mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004-D07 (1 of 2)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 37247.2 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 48.1 |  | kg/kmol | [5 empty] | 1.6586 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 5.3 / | [5 empty] | 9 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 32 |  |  | / |  |  | 284 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 3.4 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 3.4 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.954
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 427.9 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.223
|  | 26 | Density @ flowing temprature | [7 empty] | 8.355 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.0108 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | YES
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 4134(VTC)
|  | 34 | Required Area MM² | [7 empty] | 8742 (VTC)
|  | 35 | Orifice Designation | [7 empty] | Q (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 6" |  |  | in |  |  |  |  | 8" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB |  |  |  |  | (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE (VTC)
|  | 40 | Nozzle | [7 empty] | SS316 (VTC)
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2113
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 7 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2113
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0021-AN07-6"-PT | [6 empty] | V-2105
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN07 / 6mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D07
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | Yes
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 17833.11 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 5.1 / | [5 empty] | 9 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 36.92 |  |  | / |  |  | 36.92 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1.2 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1.2 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.954
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.246
|  | 26 | Density @ flowing temprature | [7 empty] | 5.97 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.011 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 2240.6 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 3421 (VTC)
|  | 35 | Orifice Designation | [7 empty] | N (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 4" |  |  | in |  |  |  |  | 6" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB |  |  |  |  | (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE (VTC)
|  | 40 | Nozzle | [7 empty] | SS316 (VTC)
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2114
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 8 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2114
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0022-AN07-6"-PT | [6 empty] | V-2105
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN07 / 6mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D07
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | Yes
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 17833.11 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.55 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 5.1 / | [5 empty] | 9 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 36.92 |  |  | / |  |  | 36.92 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1.2 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1.2 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.954
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.246
|  | 26 | Density @ flowing temprature | [7 empty] | 5.97 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.011 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 2240.6 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 3421 (VTC)
|  | 35 | Orifice Designation | [7 empty] | N (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 4" |  |  | in |  |  |  |  | 6" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB |  |  |  |  | (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE (VTC)
|  | 40 | Nozzle | [7 empty] | SS316 (VTC)
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2121A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 9 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2121A
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0029A-CN07-2"-PT | [6 empty] | V-2101A
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN07 / 6mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D07 (1 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 2166 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.55 |  | kg/kmol | [5 empty] | 0.84655 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 4.9 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 60 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.5 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.5 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.822
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.457
|  | 26 | Density @ flowing temprature | [7 empty] | 5.77 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.011 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | YES
|  | 32 | Basis of Selection | [7 empty] | Control Valve Failiure
|  | 33 | Calculated Area MM² | [7 empty] | 107.25 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.938 (VTC)
|  | 35 | Orifice Designation | [7 empty] | E (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB |  |  |  |  | (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE (VTC)
|  | 40 | Nozzle | [7 empty] | SS316 (VTC)
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2121B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 10 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2121B
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0029B-CN07-2"-PT | [6 empty] | V-2101B
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN07 / 6mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D07 (2 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 2166 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.55 |  | kg/kmol | [5 empty] | 0.84655 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 4.9 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 60 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.5 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.5 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.822
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.457
|  | 26 | Density @ flowing temprature | [7 empty] | 5.77 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.011 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | YES
|  | 32 | Basis of Selection | [7 empty] | Control Valve Failiure
|  | 33 | Calculated Area MM² | [7 empty] | 107.25 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.938 (VTC)
|  | 35 | Orifice Designation | [7 empty] | E (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB |  |  |  |  | (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE (VTC)
|  | 40 | Nozzle | [7 empty] | SS316 (VTC)
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2121C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 11 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2121C
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0029C-CN07-2"-PT | [6 empty] | V-2101C
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN07 / 6mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D06 (3 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 2166 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.55 |  | kg/kmol | [5 empty] | 0.84655 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 4.9 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 60 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.5 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.5 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.822
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.457
|  | 26 | Density @ flowing temprature | [7 empty] | 5.77 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.011 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | YES
|  | 32 | Basis of Selection | [7 empty] | Control Valve Failiure
|  | 33 | Calculated Area MM² | [7 empty] | 107.25 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.938 (VTC)
|  | 35 | Orifice Designation | [7 empty] | E (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB |  |  |  |  | (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE (VTC)
|  | 40 | Nozzle | [7 empty] | SS316 (VTC)
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2122A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 12 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2122A
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0032A-CN05-3"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D07(1 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 19 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 124.8 |  |  | / |  |  | 124.8 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.9 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.9 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.964
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 693.3 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.225
|  | 26 | Density @ flowing temprature | [7 empty] | 15.38 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.01489 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 539.85 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 1017(VTC)
|  | 35 | Orifice Designation | [7 empty] | J (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2122B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 13 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2122B
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0032B-CN05-3"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D07 (2 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 19 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 124.8 |  |  | / |  |  | 124.8 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.9 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.9 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.964
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 693.3 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.225
|  | 26 | Density @ flowing temprature | [7 empty] | 15.38 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.01489 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 539.85 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 1017(VTC)
|  | 35 | Orifice Designation | [7 empty] | J (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2122C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 14 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2122C
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0032C-CN05-3"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D07 (3 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 19 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 124.8 |  |  | / |  |  | 124.8 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.9 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.9 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.964
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 693.3 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.225
|  | 26 | Density @ flowing temprature | [7 empty] | 15.38 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.01489 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 539.85 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 1017(VTC)
|  | 35 | Orifice Designation | [7 empty] | J (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2123A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 15 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2123A
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0033A-CN05-3"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D07(1 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 19 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 124.8 |  |  | / |  |  | 124.8 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.9 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.9 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.964
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 693.3 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.225
|  | 26 | Density @ flowing temprature | [7 empty] | 15.38 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.01489 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 539.85 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 1017(VTC)
|  | 35 | Orifice Designation | [7 empty] | J (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2123B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 16 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2123B
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0033B-CN05-3"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D07 (2 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 19 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 124.8 |  |  | / |  |  | 124.8 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.9 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.9 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.964
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 693.3 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.225
|  | 26 | Density @ flowing temprature | [7 empty] | 15.38 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.01489 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 539.85 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 1017(VTC)
|  | 35 | Orifice Designation | [7 empty] | J (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGEDRF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2123C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 17 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2123C
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0033C-CN05-3"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D07 (3 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 19 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 124.8 |  |  | / |  |  | 124.8 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.9 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.9 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.964
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 693.3 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.225
|  | 26 | Density @ flowing temprature | [7 empty] | 15.38 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.01489 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 539.85 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 1017(VTC)
|  | 35 | Orifice Designation | [7 empty] | J (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2131A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 18 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2131A
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0042A-CN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D07 (1 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 982.27 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 18.1 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 208 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 3.4 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 3.4 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.936
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 18.08 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.013 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | YES
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 59.62 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.93 (VTC)
|  | 35 | Orifice Designation | [7 empty] | D (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE( (VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2131B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 19 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2131B
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0042B-CN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D07 (2 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 982.27 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 18.1 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 208 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 3.4 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 3.4 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.936
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 18.08 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.013435 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | YES
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 59.62 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.93 (VTC)
|  | 35 | Orifice Designation | [7 empty] | D (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE(VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2131C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 20 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2131C
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0042C-CN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | CN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D06(3 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 982.27 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 18.1 / | [5 empty] | 22 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 208 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 3.4 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 3.4 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.936
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 18.8 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.013 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | YES
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 59.62 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.93 (VTC)
|  | 35 | Orifice Designation | [7 empty] | D (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE(VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D02

## PSV-2132A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 21 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2132A
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0047A-FN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | FN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D05 (1 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 54.80 / | [5 empty] | 62 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 142.3 |  |  | / |  |  | 142.3 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.923
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 566.7 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 54.0599 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.016729 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 193.67 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 397.60 (VTC)
|  | 35 | Orifice Designation | [7 empty] | G (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1 1/2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #600 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2133A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 22 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2133A
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0048A-FN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | FN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D05 (1 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 54.80 / | [5 empty] | 62 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 142.3 |  |  | / |  |  | 142.3 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.923
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 566.7 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 54.0599 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.016729 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 193.67 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 397.60 (VTC)
|  | 35 | Orifice Designation | [7 empty] | G (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1 1/2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #600 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2132B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 23 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2132B
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0047B-FN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | FN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D05 (2 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 54.80 / | [5 empty] | 62 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 142.3 |  |  | / |  |  | 142.3 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.923
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 566.7 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 54.0599 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.016729 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 193.67 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 397.60 (VTC)
|  | 35 | Orifice Designation | [7 empty] | G (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1 1/2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #600 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2133B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 24 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2133B
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0048B-FN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | FN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D05 (2 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 54.80 / | [5 empty] | 62 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 142.3 |  |  | / |  |  | 142.3 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.923
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 566.7 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 54.0599 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.016729 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 193.67 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 397.60 (VTC)
|  | 35 | Orifice Designation | [7 empty] | G (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1 1/2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #600 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2132C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 25 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2132C
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0047C-FN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | FN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D05 (3 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 54.80 / | [5 empty] | 62 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 142.3 |  |  | / |  |  | 142.3 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.923
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 566.7 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 54.0599 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.016729 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 193.67 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 397.60 (VTC)
|  | 35 | Orifice Designation | [7 empty] | G (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1 1/2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #600 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2133C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 26 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2133C
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0048C-FN05-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | FN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D05 (3 OF 3)
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 8664 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.52 |  | kg/kmol | [5 empty] | 0.84552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 54.80 / | [5 empty] | 62 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 142.3 |  |  | / |  |  | 142.3 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.923
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 566.7 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.278
|  | 26 | Density @ flowing temprature | [7 empty] | 54.0599 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.016729 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 193.67 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 397.60 (VTC)
|  | 35 | Orifice Designation | [7 empty] | G (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1 1/2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #600 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03
in Gas Compressor vendor scope of work

## PSV-2141
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 27 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2141
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0060-FN05-3"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | FN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012 _D07
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 17252.5 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.562 |  | kg/kmol | [5 empty] | 0.84697 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 53.9 / | [5 empty] | 62 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 60 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.823
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.461
|  | 26 | Density @ flowing temprature | [7 empty] | 59.17 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.014 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 311 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 629.01 (VTC)
|  | 35 | Orifice Designation | [7 empty] | H (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #600 FLANGEDRF | [7 empty] | #150 FLANGEDRF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE(VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2142
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 28 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2142
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | GAS-111-0062-FN05-3"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | FN05 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012_D07
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 17252.5 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 24.562 |  | kg/kmol | [5 empty] | 0.84697 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 53.9 / | [5 empty] | 62 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 60 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 1.1
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.823
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.461
|  | 26 | Density @ flowing temprature | [7 empty] | 59.17 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.014 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | Blocked Outlet
|  | 33 | Calculated Area MM² | [7 empty] | 311 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 629.01 (VTC)
|  | 35 | Orifice Designation | [7 empty] | H (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #600 FLANGEDRF | [7 empty] | #150 FLANGEDRF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB (VTC)
|  | 39 | Seat and Disc | [7 empty] | SS316+RPTFE(VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2201
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 29 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2201
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | ISA-112-0009-AZ00-2"-NP | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AZ00 / 0mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D07
|  | 5 | Discharge to | [7 empty] | To ATM
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | No
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 1071.8 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 28.95 |  | kg/kmol | [5 empty] | 0.99828 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 8 | [5 empty] | 12.5 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 65 |  |  | / |  |  | 323.4 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.99
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.416
|  | 26 | Density @ flowing temprature | [7 empty] | 9.29 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.021 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | Yes
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 113.24 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.95 (VTC)
|  | 35 | Orifice Designation | [7 empty] | E (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM B148 UNS C95800
|  | 39 | Seat and Disc | [7 empty] | ASTM B148 UNS C95800 | [11 empty] | 15.125
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 54 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2211A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 30 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2211A
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | NIT-112-0022-AN01-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN01 / 1mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016_D07
|  | 5 | Discharge to | [7 empty] | To ATM
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | No
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 500.39 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 28 |  | kg/kmol | [5 empty] | 0.96552 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 8 | [5 empty] | 12.5 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 60 |  |  | / |  |  | 323.4 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.5 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.5 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.99
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | - | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.4
|  | 26 | Density @ flowing temprature | [7 empty] | 9.12 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.030459 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | Yes
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 54.241 (VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.9 (VTC)
|  | 35 | Orifice Designation | [7 empty] | D (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | A216 Gr. WCB
|  | 39 | Seat and Disc | [7 empty] | 13Cr+PTFE(VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 52 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2271
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 31 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2271
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | FLG-111-0011-AN07-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN07 / 6mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022_D07
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | Yes
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Bellows
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 174.5 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 18.02 |  | kg/kmol | [5 empty] | 0.62138 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 4.9 | [5 empty] | 9 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 36.78 |  |  | / |  |  | 182.6 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 3.2 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 3.2 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.975
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 1994 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.245
|  | 26 | Density @ flowing temprature | [7 empty] | 5.77 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.012191 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 28.75(VTC)
|  | 34 | Required Area MM² | [7 empty] | 153.9 (VTC)
|  | 35 | Orifice Designation | [7 empty] | D (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1" |  |  | in |  |  |  |  | 2" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A216 GR. WCB
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE (VTC)
|  | 40 | Nozzle | [7 empty] | 316SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A216 GR. WCB (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | SS316+PTFE (VTC)
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 52 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## PSV-2293
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 32 از 33
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
PRESSURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | PSV-2293
|  | 2 | Service | [7 empty] | GAS
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | TEG-111-0113-AN04-2"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN04 / 3mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D07
|  | 5 | Discharge to | [7 empty] | To FLARE
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | Yes
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | GAS | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 2098.014 | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 143.6 |  | kg/kmol | [5 empty] | 4.9517 |  |  | kg/m3
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 0.1 | [5 empty] | 3.5 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | 33 |  |  | / |  |  | 335.9 | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.1 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.1 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 21%
|  | 22 | Over Pressure Factor | [7 empty] | 1.21
|  | 23 | Compressibility Factor(Z) | [7 empty] | 0.646
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 314.3 | [5 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.083
|  | 26 | Density @ flowing temprature | [7 empty] | 10.29 |  |  |  |  | kg/m3
|  | 27 | Operating Viscosity | [7 empty] | 0.010118 |  |  |  |  | cP
|  | 28 | Barometric Pressure | [8 empty] | 13.26 ~ 14.37 |  |  |  | psia
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | API 520 | [10 empty] | -
|  | 30 | Construction Code | [7 empty] | API 520
|  | 31 | Fire | [7 empty] | NO
|  | 32 | Basis of Selection | [7 empty] | FIRE
|  | 33 | Calculated Area MM² | [7 empty] | 275(VTC)
|  | 34 | Required Area MM² | [7 empty] | 397.6 (VTC)
|  | 35 | Orifice Designation | [7 empty] | G (VTC)
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 1 1/2" |  |  | in |  |  |  |  | 3" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A105
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE(VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A105 (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 52 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## TSV-2281
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 33 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
TEMPERATURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | TSV-2281
|  | 2 | Service | [7 empty] | LIQUID
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | DO-112-0005A-AN01-1"-PT | [6 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN01 / 1mm | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023_D07(1 OF 3)
|  | 5 | Discharge to | [7 empty] | To DIESEL OIL DRUM
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | NO
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | LIQUID | [7 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | 39.537 (V.T.C) | [8 empty] | kg/h
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp | [5 empty] | 184.4 | [5 empty] | 0.85
|  | 16 | Oper. Pressure |  |  |  | Set Pressure | [5 empty] | 0.1 | [5 empty] | 3.5 | bar-g
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. | [5 empty] | AMB |  |  | / |  |  | VTA | °C
|  | 18 | Back Pressure |  |  |  | Constant | [8 empty] | - |  |  |  | bar-g
|  | 19 |  |  |  |  | Variable | [8 empty] | 0.01 |  |  |  | bar-g
|  | 20 |  |  |  |  | Total | [8 empty] | 0.01 |  |  |  | bar-g
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 110%
|  | 23 | Compressibility Factor(Z) | [7 empty] | -
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.118
|  | 26 | Density @ flowing temprature | [7 empty] | 850
|  | 27 | Operating Viscosity (cp) | [7 empty] | 2.143
|  | 28 | Barometric Pressure | [7 empty] | 13.26 ~ 14.37
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | - | [7 empty] | -
|  | 30 | Construction Code | [7 empty] | -
|  | 31 | Fire | [7 empty] | -
|  | 32 | Basis of Selection | [7 empty] | Thermal Expansion
|  | 33 | Calculated Area MM² | [7 empty] | 0.00003464509 (V.T.C)
|  | 34 | Required Area MM² | [7 empty] | 0.0000709676 (V.T.C)
|  | 35 | Orifice Designation | [7 empty] | D
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 3/4" |  |  | in |  |  |  |  | 1" |  | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [7 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A105
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE(VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A105 (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 52 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03

## TSV-2281A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  |  | نسخه | شماره صفحه: 34 از 34
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | IN | DT |  | 0009 |  |  | D03
TEMPERATURE SAFETY VALVE
GENERAL |  | 1 | Tag Number | [7 empty] | TSV-2281A
|  | 2 | Service | [7 empty] | LIQUID
|  | 3 | Line No. |  |  |  | Vessel No. |  |  |  | CHD-112-0116-CN07-1"-PT | [5 empty] | -
|  | 4 | Pipe Class / C.A. |  |  |  | P&ID No. | P&ID No. |  |  | AN01 / 1mm | [5 empty] | BK-GCS-PEDCO-120-PR-PI-0004_D07(2 OF 2)
|  | 5 | Discharge to | [7 empty] | To Close Drain Header
|  | 6 | Protect Equipment | [7 empty] | -
|  | 7 | Area Clacification | [7 empty] | Zone 2, IIB T4
|  | 8 | NACE MR0175/ISO 15156 Compliance | [7 empty] | YES
BASIS |  | 9 | Nozzle (Full, Semi) | [7 empty] | Full Nozzle, Spring Loaded Type
|  | 10 | Design Type |  |  |  | Safety, Relief, Safety-Relief |  |  |  | Safety
|  | 11 |  |  |  |  | Conventional, bellows, Pilot Op. |  |  |  | Conventional
|  | 12 | Bonnet Type | [7 empty] | Closed
PROCESS CONDITIONS |  | 13 | Fluid |  |  |  | State |  |  |  | LIQUID | [6 empty] | Singel Phase
|  | 14 | Required Capacity | [7 empty] | VTC
|  | 15 | Molecular Mass |  |  |  | Sp. Gr.@ relief Tmp |  |  |  | 18.03 | [6 empty] | 0.5619
|  | 16 | Oper. Pressure |  |  |  | Set Pressure |  |  |  | 19.3 | [6 empty] | 24
|  | 17 | Oper. Temperature |  |  |  | RelievingTemp. |  |  |  | 32.14 | [6 empty] | 143.8
|  | 18 | Back Pressure |  |  |  | Constant |  |  |  | -
|  | 19 |  |  |  |  | Variable |  |  |  | 0
|  | 20 |  |  |  |  | Total |  |  |  | 0
|  | 21 | % Allowable Overpressure | [7 empty] | 10%
|  | 22 | Over Pressure Factor | [7 empty] | 110%
|  | 23 | Compressibility Factor(Z) | [7 empty] | -
|  | 24 | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | -
|  | 25 | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.151
|  | 26 | Density @ flowing temprature | [7 empty] | 1003
|  | 27 | Operating Viscosity (cp) | [7 empty] | 0.762
|  | 28 | Barometric Pressure | [7 empty] | 13.26 ~ 14.37
SELECTION |  | 29 | Design Code |  |  |  | Sizing Basis | Sizing Basis |  |  | - | [6 empty] | -
|  | 30 | Construction Code | [7 empty] | -
|  | 31 | Fire | [7 empty] | -
|  | 32 | Basis of Selection | [7 empty] | Thermal Expansion
|  | 33 | Calculated Area MM² | [7 empty] | VTC
|  | 34 | Required Area MM² | [7 empty] | VTC
|  | 35 | Orifice Designation | [7 empty] | D
CONNECTIONS |  | 36 | Size: Inlet |  |  |  | Outlet |  |  |  | 3/4" |  |  | in |  |  |  | 1" | in
|  | 37 | Rating & Facing :In |  |  |  | Outlet |  |  |  | #300 FLANGED RF | [6 empty] | #150 FLANGED RF
MATERIALS (VTC) |  | 38 | Body and Bonnet | [7 empty] | ASTM A105
|  | 39 | Seat and Disc | [7 empty] | SS316+PTFE(VTC)
|  | 40 | Nozzle | [7 empty] | 316 SS
|  | 41 | Guide and Rings | [7 empty] | VTA
|  | 42 | Spring | [7 empty] | ASTM A105 (VTC) (Note2)
|  | 43 | Bellows | [7 empty] | N/A
44
OPTIONS |  | 45 | Cap: Screwed or Bolted | [7 empty] | Screwed
|  | 46 | Lever: Plain or Packed | [7 empty] | N/A
|  | 47 | Test Gage | [7 empty] | Yes
|  | 48 | With Rupture Disc | [7 empty] | No
|  | 49 | Hydro Test | [7 empty] | Required
|  | 50 | Seat Leakage Test | [7 empty] | Required
|  | 51 | Compliance Standard | [7 empty] | N/A
PURCHASE (will be finalized later) |  | 52 | Manufacturer | [7 empty] | Will Be Finalized Later
|  | 53 | Model | [7 empty] | Will Be Finalized Later
|  | 52 | Serial No. | [7 empty] | Will Be Finalized Later
Notes:
| VTA : Vendor to Advise in bidding stage |  |  |  |  | VTC : Vendor to confirm in bidding stage | [6 empty] | N/A: Not applicable
1- For material details refer to "Piping Material Specification Doc No." BK-GCS-PEDCO-120-PI-SP-0001-D03 ".
2- Suitable coating such as cadmiun plated shall be considered ( vendor to advise)
D03